Consolidation Period:  From July 1, 2007 to the e-Laws currency date.

This Regulation is made in English only.

Division B

Part 1
General

| Section | 1.1. | General |
| --- | --- | --- |
|  | 1.1.1. | Application |
|  | 1.1.2. | Climatic Data |
| Section | 1.2. | Reserved |
| Section | 1.3. | Referenced Documents and Organizations |
|  | 1.3.1. | Referenced Documents |
|  | 1.3.2. | Abbreviations |

Section 1.1.  General

1.1.1.  Application

1.1.1.1.  Application

(1)  This Part applies to all buildings covered in this Code.

1.1.2.  Climatic Data

1.1.2.1.  Climatic and Seismic Design Values

(1)  The climatic and seismic values required for the design of buildings under this Code shall be in conformance with the climatic and seismic values provided in Supplementary Standard SB-1.

(2)  The outside winter design temperatures determined from Supplementary Standard SB-1 shall be those listed for the January 2.5% values.

1.1.2.2.  Depth of Frost Penetration

(1)  Depth of frost penetration shall be established on the basis of local experience.

Section 1.2.  Reserved

Section 1.3.  Referenced Documents and Organizations

1.3.1.  Referenced Documents

1.3.1.1.  Effective Date

(1)  Unless otherwise specified in this Code, the documents referenced in this Code shall include all amendments, revisions and supplements effective to May 31, 2006.

1.3.1.2.  Applicable Editions

(1)  Where documents are referenced in this Code, they shall be in the editions designated in Column 2 of Table 1.3.1.2.

Table 1.3.1.2.
Documents Referenced in the Building Code

Forming Part of Sentence 1.3.1.2.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| Issuing Agency | Document Number | Title of Document | Code Reference |
| ACGIH | 2004, 25th Edition | Industrial Ventilation Manual | 6.2.1.1.(1) |
| ANSI | A208.1-1999 | Particleboard, Mat-Formed Wood | Table 5.10.1.1. |
|  |  |  | 9.23.14.2.(3) |
|  |  |  | 9.29.9.1.(1) |
|  |  |  | 9.30.2.2.(1) |
| ANSI | B16.18-2001 | Cast Copper Alloy Solder Joint Pressure Fittings | 7.2.7.6.(1) |
|  |  |  | 7.2.7.6.(2) |
|  |  |  | Table 7.2.11.2. |
| ANSI/ASME | A112.19.8M-1987 | Suction Fittings for Use in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Whirlpool Bathtub Appliances | 3.12.4.1.(9) |
| ANSI/ASME | B16.3-1998 | Malleable Iron Threaded Fittings | 7.2.6.6.(1) |
| ANSI/ASME | B16.4-1998 | Gray Iron Threaded Fittings | 7.2.6.5.(1) |
|  |  |  | Table 7.2.11.2. |
| ANSI/ASME | B16.12-1998 | Cast Iron Threaded Drainage Fittings | 7.2.6.3.(1) |
| ANSI/ASME | B16.15-1985 | Cast Bronze Threaded Fittings, Classes 125 and 250 | 7.2.7.3.(1) |
| ANSI/ASME | B16.22-2001 | Wrought Copper and Copper Alloy Solder Joint Pressure Fittings | 7.2.7.6.(1) |
| ANSI/ASME | B16.24-2001 | Cast Copper Alloy Pipe Flanges and Flanged Fittings: Classes 150, 300, 400, 600, 900, 1500 and 2500 | 7.2.7.2.(1) |
| ANSI/ASME | B16.26-1988 | Cast Copper Alloy Fittings for Flared Copper Tubes | 7.2.7.7.(1) |
|  |  |  | 7.2.7.7.(2) |
|  |  |  | Table 7.2.11.2. |
| ANSI/ASME | B16.29-2001 | Wrought Copper and Wrought Copper Alloy Solder Joint Drainage Fittings - DWV | 7.2.7.5.(1) |
| ANSI/ASME | B18.6.1-1981 | Wood Screws (Inch Series) | Table 5.10.1.1. |
|  |  |  | 9.23.3.1.(2) |
| ANSI/ASHRAE | 62-2001 | Ventilation for Acceptable Indoor Air Quality | 6.2.2.1.(2) |
| ANSI/ASHRAE/IESNA | 90.1-2004 | Energy Standard for Buildings Except Low-Rise Residential Buildings | 6.2.2.1.(1) |
|  |  |  | 12.2.1.1.(2) |
| ANSI/AWWA | C104 / A21.4-2004 | Cement-Mortar Lining for Ductile-Iron Pipe Fittings for Water | 7.2.6.4.(2) |
|  |  |  | Table 7.2.11.2. |
| ANSI/AWWA | C110 / A21.10-2003 | Ductile-Iron and Gray-Iron Fittings, 3 in. Through 48 in. (75 mm Through 1200 mm), for Water and Other Liquids | 7.2.6.4.(3) |
|  |  |  | Table 7.2.11.2. |
| ANSI/AWWA | C111 / A21.11-2000 | Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fitting | 7.2.6.4.(4) |
|  |  |  | Table 7.2.11.2. |
| ANSI/AWWA | C151 / A21.51-2002 | Ductile-Iron Pipe, Centrifugally Cast, for Water | 7.2.6.4.(1) |
|  |  |  | Table 7.2.11.2. |
| ANSI/CSA | ANSI Z21.22-1999 / CSA 4.4-M99 including | Relief Valves for Hot Water Supply Systems | 7.2.10.11.(1) |
|  | Addenda 1 |  |  |
|  | ANSI Z21.22a-2000 / |  |  |
|  | CSA 4.4a -2000 |  |  |
|  | Addenda 2 |  |  |
|  | ANSI Z21.22b-2001 / |  |  |
|  | CSA 4.4b-2001 |  |  |
| APHA/AWWA/ WEF | 2005, 21st Edition | Standard Methods for the Examination of Water and Waste Water | 8.9.2.4.(1)(b) |
| ASHRAE | 2005 | Fundamentals | 6.2.1.1.(1) |
| ASHRAE | 2003 | HVAC Applications | 6.2.1.1.(1) |
| ASHRAE | 2004 | HVAC Systems and Equipment | 6.2.1.1.(1) |
| ASHRAE | 2002 | Refrigeration | 6.2.1.1.(1) |
| ASME | B16.23-2002 | Cast Copper Alloy Solder Joint Drainage Fittings: DWV | 7.2.7.5.(1) |
| ASSE | 1010-2004 | Water Hammer Arresters | 7.2.10.15.(1) |
| ASSE | 1051-2002 | Individual and Branch Type Air Admittance Valves for Sanitary Drainage Systems | 7.2.10.16.(1) |
| ASTM | A53 / A53M-02 | Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless | 7.2.6.7.(4) |
| ASTM | A123 / A123M-02 | Zinc (Hot Dip Galvanized) Coatings on Iron and Steel Products | Table 5.10.1.1. |
|  |  |  | Table 9.20.16.1. |
| ASTM | A153 / A153M-03 | Zinc Coating (Hot-Dip) on Iron and Steel Hardware | Table 5.10.1.1. |
|  |  |  | Table 9.20.16.1. |
| ASTM | A252-98 | Welded and Seamless Steel Pipe Piles | 4.2.3.8.(1) |
| ASTM | A283 / A283M-03 | Low and Intermediate Tensile Strength Carbon Steel Plates | 4.2.3.8.(1) |
| ASTM | A518 / A518M-99 | Corrosion-Resistant High-Silicon Iron Castings | 7.2.8.1.(1) |
| ASTM | A653 / A653M-03 | Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process | Table 5.10.1.1. |
|  |  |  | 9.3.3.2.(1) |
| ASTM | A792 / A792M-03 | Steel Sheet, 55% Aluminum-Zinc Alloy-Coated by the Hot-Dip Process | 9.3.3.2.(1) |
| ASTM | A1008 / A1008M-04 | Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low Alloy with Improved Formability | 4.2.3.8.(1) |
| ASTM | A1011 / A1011M-03a | Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low Alloy with Improved Formability | 4.2.3.8.(1) |
| ASTM | B32-03 | Solder Metal | 7.2.9.2.(2) |
| ASTM | B42-02e1 | Seamless Copper Pipe, Standard Sizes | 7.2.7.1.(1) |
| ASTM | B43-98e1 | Seamless Red Brass Pipe, Standard Sizes | 7.2.7.1.(2) |
| ASTM | B68-02 | Seamless Copper Tube, Bright Annealed | 7.2.7.4.(3) |
| ASTM | B88-03 | Seamless Copper Water Tube | 7.2.7.4.(1) |
|  |  |  | Table 7.2.11.2. |
| ASTM | B306-02 | Copper Drainage Tube (DWV) | 7.2.7.4.(1) |
| ASTM | B813-00e1 | Liquid and Paste Fluxes for Soldering of Copper and Copper Alloy and Tube | 7.2.9.2.(3) |
| ASTM | B828-02 | Making Capillary Joints by Soldering of Copper and Copper Alloy Tube and Fittings | 7.3.2.4.(1) |
| ASTM | C4-03 | Clay Drain Tile and Perforated Clay Drain Tile | Table 5.10.1.1. |
|  |  |  | 9.14.3.1.(1) |
| ASTM | C27-98 | Classification for Fire Clay and High-Alumina Refractory Brick | 9.21.3.4.(1) |
| ASTM | C36 / C36M-03 | Gypsum Wallboard | 3.1.5.12.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C37 / C37M-01 | Gypsum Lath | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C79 / C79M-04 | Treated Core and Nontreated Core Gypsum Sheathing Board | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C126-99 | Ceramic Glazed Structural Clay Facing Tile, Facing Brick, and Solid Masonry Units | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| ASTM | C212-00 | Structural Clay Facing Tile | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| ASTM | C260-01 | Air-Entraining Admixtures for Concrete | 9.3.1.8.(1) |
| ASTM | C411-97 | Hot-Surface Performance of High-Temperature Thermal Insulation | 6.2.3.4.(3) |
|  |  |  | 6.2.9.2.(2) |
| ASTM | C412M-03 | Concrete Drain Tile (Metric) | Table 5.10.1.1. |
|  |  |  | 9.14.3.1.(1) |
| ASTM | C442 / C442M-04 | Gypsum Backing Board, and Gypsum Coreboard, and Gypsum Shaftliner Board | 3.1.5.12.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C444M-03 | Perforated Concrete Pipe (Metric) | Table 5.10.1.1. |
|  |  |  | 9.14.3.1.(1) |
| ASTM | C494 / C494M-04 | Chemical Admixtures for Concrete | 9.3.1.8.(1) |
| ASTM | C588 / C588M-03 | Gypsum Base for Veneer Plasters | 3.1.5.12.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C630 / C630M-03 | Water-Resistant Gypsum Backing Board | 3.1.5.12.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C700-02 | Vitrified Clay Pipe, Extra Strength, Standard Strength and Perforated | Table 5.10.1.1. |
|  |  |  | 9.14.3.1.(1) |
| ASTM | C931 / C931M-04 | Exterior Gypsum Soffit Board | 3.1.5.12.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C960 / C960M-04 | Predecorated Gypsum Board | 3.1.5.11.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C1002-01 | Steel Self-Piercing Tapping Screws for the Application of Gypsum Panel Products or Metal Plaster Bases to Wood Studs or Steel Studs | Table 5.10.1.1. |
|  |  |  | 9.24.1.4.(1) |
|  |  |  | 9.29.5.7.(1) |
| ASTM | C1053-00 | Borosilicate Glass Pipe and Fittings for Drain, Waste and Vent (DWV) Applications | 7.2.8.1.(1) |
| ASTM | C1177 / C1177M-04e1 | Glass Mat Gypsum Substrate for Use as Sheathing | Table 5.10.1.1. |
|  |  |  | Table 9.23.16.2.A. |
| ASTM | C1178 / C1178M-04 | Glass Mat Water-Resistant Gypsum Backing Panel | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C1395 / C1395M-04 | Gypsum Ceiling Board | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | C1396 / C1396M-03a | Gypsum Board | Table 5.10.1.1. |
|  |  |  | 9.29.5.2.(1) |
| ASTM | D374-99 | Thickness of Solid Electrical Insulation | 3.15.4.1.(1)(c) |
| ASTM | D568-77 | Rate of Burning and/or Extent and Time of Burning of Flexible Plastics in a Vertical Position | 3.15.4.1.(1)(b) |
| ASTM | D635-03 | Rate of Burning and/or Extent and Time of Burning of Plastics in a Horizontal Position | 3.15.4.1.(1)(a) |
| ASTM | D2178-97a | Asphalt Glass Felt Used in Roofing and Waterproofing | Table 5.10.1.1. |
| ASTM | D2898-94 | Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing | 3.1.5.5.(4) |
|  |  |  | 3.1.5.21.(1) |
| ASTM | D3261-03 | Butt Heat Fusion Polyethylene (PE) Plastic Fittings for Polyethylene (PE) Plastic Pipe and Tubing | 7.2.5.5.(3) |
| ASTM | E90-04 | Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements | 5.9.1.1.(1) |
|  |  |  | 9.11.1.1.(1) |
| ASTM | E96-00e1 | Water Vapour Transmission of Materials | 5.5.1.2.(3) |
|  |  |  | 9.25.1.2.(1) |
|  |  |  | 9.25.4.2.(1) |
|  |  |  | 9.30.1.2.(1) |
| ASTM | E283-04 | Determining the Rate of Air Leakage through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differentiation Across the Specimen | 9.6.5.4.(1) |
|  |  |  | 9.6.5.5.(1) |
|  |  |  | 9.7.1.7.(1) |
|  |  |  | 12.3.3.13.(1) |
| ASTM | E336-97e1 | Measurement of Airborne Sound Insulation in Buildings | 5.9.1.1.(1) |
|  |  |  | 9.11.1.1.(1) |
| ASTM | E413-87 | Classification for Rating Sound Insulation | 5.9.1.1.(1) |
|  |  |  | 9.11.1.1.(1) |
| ASTM | E2190-02 | Insulating Glass Unit Performance and Evaluation | 9.7.3.1.(1) |
| ASTM | F476-84 | Security of Swinging Door Assemblies | 9.6.8.10.(1) |
| ASTM | F628-01 | Acrylonitrile-Butadiene-Styrene (ABS) Schedule 40 Plastic Drain, Waste, and Vent Pipe With a Cellular Core | 7.2.5.10.(1) |
|  |  |  | 7.2.5.12.(1) |
| ASTM | F714-03 | Polyethylene (PE) Plastic Pipe (SDR-PR) Based on Outside Diameter | 7.2.5.6.(1) |
| AWPA | M4-02 | Care of Preservative-Treated Wood Products | 4.2.3.2.(2) |
|  |  |  | Table 5.10.1.1. |
| BNQ | NQ3624-115-2000 | Polyethylene (PE) Pipe and Fittings - Flexible Corrugated Pipes for Drainage - Characteristics and Test Methods | Table 5.10.1.1. |
|  |  |  | 9.14.3.1.(1) |
| CCBFC | NRCC 38730 | Model National Energy Code for Buildings 1997 | 6.2.2.1.(1) |
|  |  |  | 12.2.1.1.(2) |
|  |  |  | 12.2.1.2.(2) |
| CCBFC | NRCC 47666 | National Building Code of Canada, 2005 | 1.3.1.2.(3) of Division A |
|  |  |  | 2.4.2.2.(1)(b)(iii) of Division C |
| CCBFC | NRCC 47677 | National Fire Code of Canada 2005 | 3.3.1.2.(1) |
|  |  |  | 3.3.5.2.(1) |
|  |  |  | 6.2.2.5.(1) |
| CCBFC | NRCC 38732 | National Farm Building Code of Canada 1995 | 1.3.1.2.(1) of Division A |
|  |  |  | 1.3.1.2.(2) of Division A |
|  |  |  | 1.3.1.2.(3) of Division A |
|  |  |  | 1.3.1.2.(4) of Division A |
|  |  |  | 4.4.5.1.(1) |
| CCBFC | NRCC 47668 | National Plumbing Code of Canada, 2005 | 2.4.2.2.(1)(b)(iii) of Division C |
| CGSB | CAN/CGSB-1.501-M89 | Method of Permeance of Coated Wallboard | 5.5.1.2.(2) |
|  |  |  | 9.25.4.2.(6) |
| CGSB | CAN/CGSB-7.1-98 | Lightweight Steel Wall Framing Components | 9.24.1.2.(1) |
| CGSB | CAN/CGSB-7.2-97 | Adjustable Steel Columns | 9.17.3.4.(1) |
| CGSB | CAN/CGSB-10.3-92 | Air Setting Refractory Mortar | 9.21.3.4.(2) |
|  |  |  | 9.21.3.9.(1) |
|  |  |  | 9.22.2.2.(2) |
| CGSB | CAN/CGSB-11.3-M87 | Hardboard | Table 5.10.1.1. |
|  |  |  | 9.27.10.1.(2) |
|  |  |  | 9.29.7.1.(1) |
|  |  |  | 9.30.2.2.(1) |
| CGSB | CAN/CGSB-11.5-M87 | Hardboard, Precoated, Factory Finished, for Exterior Cladding | Table 5.10.1.1. |
|  |  |  | 9.27.10.1.(1) |
| CGSB | CAN/CGSB-12.1-M90 | Tempered or Laminated Safety Glass | 3.3.1.19.(2) |
|  |  |  | 3.4.6.14.(1) |
|  |  |  | 3.4.6.14.(3) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.6.6.2.(2) |
|  |  |  | 9.7.3.1.(1) |
|  |  |  | 9.8.8.7.(1) |
| CGSB | CAN/CGSB-12.2-M91 | Flat, Clear Sheet Glass | Table 5.10.1.1. |
|  |  |  | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.3-M91 | Flat, Clear Float Glass | Table 5.10.1.1. |
|  |  |  | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.4-M91 | Heat Absorbing Glass | Table 5.10.1.1. |
|  |  |  | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.5-M86 | Mirrors, Silvered | 9.6.6.3.(2) |
| CGSB | CAN/CGSB-12.8-97 | Insulating Glass Units | Table 5.10.1.1. |
|  |  |  | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.10-M76 | Glass, Light and Heat Reflecting | Table 5.10.1.1. |
|  |  |  | 9.7.3.1.(1) |
| CGSB | CAN/CGSB-12.11-M90 | Wired Safety Glass | 3.3.1.19.(2) |
|  |  |  | 3.4.6.14.(1) |
|  |  |  | 3.4.6.14.(3) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.6.6.2.(2) |
|  |  |  | 9.7.3.1.(1) |
|  |  |  | 9.8.8.7.(1) |
| CGSB | CAN/CGSB-12.20-M89 | Structural Design of Glass for Buildings | 4.3.6.1.(1) |
|  |  |  | 9.7.3.2.(1) |
| CGSB | 19-GP-5M-1984 | Sealing Compound, One Component, Acrylic Base, Solvent Curing | Table 5.10.1.1. |
|  |  |  | 9.27.4.2.(2) |
| CGSB | CAN/CGSB-19.13-M87 | Sealing Compound, One Component, Elastomeric, Chemical Curing | Table 5.10.1.1. |
|  |  |  | 9.27.4.2.(2) |
| CGSB | 19-GP-14M-1984 | Sealing Compound, One Component, Butyl-Polyisobutylene Polymer Base, Solvent Curing | Table 5.10.1.1. |
|  |  |  | 9.27.4.2.(2) |
| CGSB | CAN/CGSB-19.22-M89 | Mildew Resistant Sealing Compound for Tubs and Tile | 9.29.10.5.(1) |
| CGSB | CAN/CGSB-19.24-M90 | Multicomponent, Chemical-Curing Sealing Compound | Table 5.10.1.1. |
|  |  |  | 9.27.4.2.(2) |
| CGSB | CAN/CGSB-34.4-M89 | Siding, Asbestos-Cement, Shingles and Clapboards | Table 5.10.1.1. |
|  |  |  | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.5-M89 | Sheets, Asbestos-Cement, Corrugated | Table 5.10.1.1. |
|  |  |  | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.9-M94 | Asbestos-Cement Sewer Pipe | 7.2.5.1.(2) |
| CGSB | CAN/CGSB-34.14-M89 | Sheets, Asbestos-Cement, Decorative | Table 5.10.1.1. |
|  |  |  | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.16-M89 | Sheets, Asbestos-Cement, Flat, Fully Compressed | Table 5.10.1.1. |
|  |  |  | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.17-M89 | Sheets, Asbestos-Cement, Flat, Semicompressed | Table 5.10.1.1. |
|  |  |  | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.21-M89 | Panels, Sandwich, Asbestos-Cement with Insulating Cores | Table 5.10.1.1. |
|  |  |  | 9.27.8.1.(1) |
| CGSB | CAN/CGSB-34.22-94 | Asbestos-Cement Drain Pipe | Table 5.10.1.1. |
|  |  |  | 7.2.5.1.(1) |
|  |  |  | 9.14.3.1.(1) |
| CGSB | CAN/CGSB-34.23-94 | Asbestos-Cement House Connection Sewer Pipe | 7.2.5.1.(2) |
| CGSB | CAN/CGSB-37.1-M89 | Chemical Emulsified Type, Emulsified Asphalt for Dampproofing | Table 5.10.1.1. |
|  |  |  | 9.13.2.2.(1) |
| CGSB | CAN/CGSB-37.2-M88 | Emulsified Asphalt, Mineral Colloid Type, Unfilled, for Dampproofing and Waterproofing and for Roof Coatings | Table 5.10.1.1. |
|  |  |  | 9.13.2.2.(1) |
|  |  |  | 9.13.3.2.(1) |
| CGSB | CAN/CGSB-37.3-M89 | Application of Emulsified Asphalts for Dampproofing or Waterproofing | 5.8.2.3.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.13.2.3.(1) |
|  |  |  | 9.13.3.3.(1) |
| CGSB | CAN/CGSB-37.4-M89 | Fibrated, Cutback Asphalt, Lap Cement for Asphalt Roofing | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-37.5-M89 | Cutback Asphalt Plastic Cement | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | 37-GP-6Ma-1983 | Asphalt, Cutback, Unfilled, for Dampproofing | 5.8.2.2.(6) |
|  |  |  | 5.8.2.2.(7) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.13.2.2.(1) |
| CGSB | CAN/CGSB-37.8-M88 | Asphalt, Cutback, Filled, for Roof Coating | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | 37-GP-9Ma-1983 | Primer, Asphalt, Unfilled, for Asphalt Roofing, Dampproofing and Waterproofing | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | 37-GP-12Ma-1984 | Application of Unfilled Cutback Asphalt for Dampproofing | 5.8.2.3.(2) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.13.2.3.(1) |
| CGSB | CAN/CGSB-37.16-M89 | Filled, Cutback Asphalt for Dampproofing and Waterproofing | Table 5.10.1.1. |
|  |  |  | 9.13.2.2.(1) |
|  |  |  | 9.13.3.2.(1) |
| CGSB | 37-GP-18Ma-1985 | Tar, Cutback, Unfilled, for Dampproofing | 5.8.2.2.(6) |
|  |  |  | 5.8.2.2.(7) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.13.2.2.(1) |
| CGSB | 37-GP-21M-1985 | Tar, Cutback, Fibrated, For Roof Coating | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-37.22-M89 | Application of Unfilled, Cutback Tar Foundation Coating for Dampproofing | 5.8.2.3.(2) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.13.2.3.(1) |
| CGSB | 37-GP-36M-1976 | Application of Filled Cutback Asphalt for Dampproofing and Waterproofing | 5.8.2.3.(1) |
|  |  |  | Table 5.10.1.1. |
| CGSB | 37-GP-37M-1977 | Application of Hot Asphalt for Dampproofing or Waterproofing | 5.8.2.3.(1) |
|  |  |  | Table 5.10.1.1. |
| CGSB | CAN/CGSB-37.50-M89 | Hot Applied, Rubberized Asphalt for Roofing and Waterproofing | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-37.51-M90 | Application for Hot Applied Rubberized Asphalt for Roofing and Waterproofing | 5.6.1.3.(1) |
|  |  |  | 5.8.2.3.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.26.15.1.(1) |
| CGSB | 37-GP-52M-1984 | Roofing and Waterproofing Membrane, Sheet Applied, Elastomeric | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-37.54-95 | Polyvinyl Chloride Roofing and Waterproofing Membrane | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | 37-GP-55M-1979 | Application of Sheet Applied Flexible Polyvinyl Chloride Roofing Membrane | 5.6.1.3.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.26.16.1.(1) |
| CGSB | 37-GP-56M-1985 | Membrane, Modified, Bituminous, Prefabricated, and Reinforced for Roofing | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | 37-GP-64M-1977 | Mat Reinforcing, Fibrous Glass, for Membrane Waterproofing Systems and Built-up Roofing | Table 5.10.1.1. |
| CGSB | 41-GP-6M-1983 | Sheets, Thermosetting Polyester Plastics, Glass Fiber Reinforced | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CGSB | CAN/CGSB-41.24-95 | Rigid Vinyl Siding, Soffits and Fascia | Table 5.10.1.1. |
|  |  |  | 9.27.13.1.(1) |
| CGSB | CAN/CGSB-51.25-M87 | Thermal Insulation, Phenolic, Faced | Table 5.10.1.1. |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.25.2.2.(1) |
| CGSB | 51-GP-27M-1979 | Thermal Insulation, Polystyrene, Loose Fill | Table 5.10.1.1. |
|  |  |  | 9.25.2.2.(1) |
| CGSB | CAN/CGSB-51.32-M77 | Sheathing, Membrane, Breather Type | Table 5.10.1.1. |
|  |  |  | 9.20.13.9.(1) |
|  |  |  | 9.26.2.1.(1) |
|  |  |  | 9.27.3.2.(1) |
| CGSB | CAN/CGSB-51.33-M89 | Vapour Barrier, Sheet, Excluding Polyethylene, for Use in Building Construction | Table 5.10.1.1. |
|  |  |  | 9.25.4.2.(5) |
| CGSB | CAN/CGSB-51.34-M86 (amended 1988) | Vapour Barrier, Polyethylene Sheet for Use in Building Construction | Table 5.10.1.1. |
|  |  |  | 9.13.2.2.(1) |
|  |  |  | 9.13.4.2.(1) |
|  |  |  | 9.18.6.2.(1) |
|  |  |  | 9.25.3.2.(2) |
|  |  |  | 9.25.4.2.(4) |
| CGSB | CAN/CGSB-63.14-M89 | Plastic Skylights | 5.10.1.1.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.7.7.1.(1) |
|  |  |  | 9.7.7.2.(1) |
| CGSB | CAN/CGSB-82.1-M89 | Sliding Doors | Table 5.10.1.1. |
|  |  |  | 9.6.5.2.(1) |
| CGSB | CAN/CGSB-82.5-M88 | Insulated Steel Doors | Table 5.10.1.1. |
|  |  |  | 9.6.5.3.(1) |
| CGSB | CAN/CGSB-82.6-M86 | Doors, Mirrored Glass, Sliding or Folding, Wardrobe | 9.6.6.3.(1) |
| CGSB | CAN/CGSB-93.1-M85 | Sheet, Aluminum Alloy, Prefinished Residential | Table 5.10.1.1. |
|  |  |  | 9.27.12.1.(4) |
| CGSB | CAN/CGSB-93.2-M91 | Prefinished Aluminum Siding, Soffits and Facsia for Residential Use | Table 5.10.1.1. |
|  |  |  | 9.27.12.1.(3) |
| CGSB | CAN/CGSB-93.3-M91 | Prefinished Galvanized and Aluminum-Zinc Alloy Steel Sheet for Residential Use | Table 5.10.1.1. |
|  |  |  | 9.27.12.1.(2) |
| CGSB | CAN/CGSB-93.4-92 | Galvanized Steel and Aluminum-Zinc Alloy Coated Steel Siding, Soffits and Fascia, Prefinished, Residential | Table 5.10.1.1. |
|  |  |  | 9.27.12.1.(1) |
| CSA | CAN/CSA-6.19-01 | Residential Carbon Monoxide Alarming Devices | 6.2.12.3.(1) |
|  |  |  | 9.33.4.3.(1) |
| CSA | CAN/CSA-A23.1-04 | Concrete Materials and Methods of Concrete Construction | 4.2.3.6.(1) |
|  |  |  | 4.2.3.9.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.3.1.1.(4) |
|  |  |  | 9.3.1.3.(1) |
|  |  |  | 9.3.1.4.(1) |
|  |  |  | 9.40.1.4.(1) |
| CSA | A23.3-04 | Design of Concrete Structures | Table 4.1.8.9. |
|  |  |  | 4.3.3.1.(1) |
| CSA | A60.1-M1976 | Vitrified Clay Pipe | 7.2.5.4.(1) |
| CSA | A60.3-M1976 | Vitrified Clay Pipe Joints | 7.2.5.4.(2) |
| CSA | CAN/CSA-A82.1-M87 | Burned Clay Brick (Solid Masonry Units Made From Clay or Shale) | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | A82.3-M1978 | Calcium Silicate (Sand-Lime) Building Brick | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | A82.4-M1978 | Structural Clay Load-Bearing Wall Tile | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | A82.5-M1978 | Structural Clay Non-Load-Bearing Tile | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | CAN3-A82.8-M78 | Hollow Clay Brick | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | CAN/CSA-A82.27-M91 | Gypsum Board | 3.1.5.12.(4) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.29.5.2.(1) |
| CSA | A82.30-M1980 | Interior Furring, Lathing and Gypsum Plastering | Table 5.10.1.1. |
|  |  |  | 9.29.4.1.(1) |
| CSA | A82.31-M1980 | Gypsum Board Application | Table 5.10.1.1. |
|  |  |  | 9.10.12.4.(3) |
|  |  |  | 9.29.5.1.(2) |
| CSA | CAN3-A93-M82 | Natural Airflow Ventilators for Buildings | Table 5.10.1.1. |
|  |  |  | 9.19.1.2.(5) |
| CSA | CAN/CSA-A123.1-98 | Asphalt Shingles Made from Organic Felt and Surfaced with Mineral Granules | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CSA | A123.2-03 | Asphalt Coated Roofing Sheets | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CSA | CAN/CSA-A123.3-98 | Asphalt Saturated Organic Roofing Felt | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CSA | CAN/CSA-A123.4-04 | Asphalt for Constructing Built-Up Roof Coverings and Waterproofing Systems | Table 5.10.1.1. |
|  |  |  | 9.13.2.2.(1) |
|  |  |  | 9.13.3.2.(1) |
|  |  |  | 9.26.2.1.(1) |
| CSA | CAN/CSA-A123.5-98 | Asphalt Shingles Made from Glass Felt and Surfaced with Mineral Granules | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CSA | A123.17-1963 | Asphalt-Saturated Felted Glass-Fibre Mat for Use in Construction of Built-Up Roofs | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CSA | CAN3-A123.51-M85 | Asphalt Shingle Application on Roof Slopes 1:3 and Steeper | 5.6.1.3.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.26.1.2.(1) |
| CSA | CAN3-A123.52-M85 | Asphalt Shingle Application on Roof Slopes 1:6 to Less than 1:3 | 5.6.1.3.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.26.1.2.(1) |
| CSA | A165.1-04 | Concrete Block Masonry Units | Table 5.10.1.1. |
|  |  |  | 9.15.2.2.(1) |
|  |  |  | 9.17.5.1.(1) |
|  |  |  | 9.20.2.1.(1) |
|  |  |  | 9.20.2.6.(1) |
| CSA | A165.2-04 | Concrete Brick Masonry Units | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | A165.3-04 | Prefaced Concrete Masonry Units | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | CAN3-A165.4-M85 | Autoclaved Cellular Units | Table 5.10.1.1. |
|  |  |  | 9.20.2.1.(1) |
| CSA | A179-04 | Mortar and Grout for Unit Masonry | Table 5.10.1.1. |
|  |  |  | 9.15.2.2.(3) |
|  |  |  | 9.20.3.1.(1) |
| CSA | CAN/CSA-A220.0-M91 | Performance of Concrete Roof Tiles | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
| CSA | CAN/CSA-A220.1-M91 | Installation of Concrete Roof Tiles | Table 5.10.1.1. |
|  |  |  | 9.26.17.1.(1) |
| CSA | A257 Series-03 | Standards for Concrete Pipe and Manhole Sections | 7.2.5.3.(1) |
| CSA | A257.4-03 | Precast Reinforced Circular Concrete Manhole Sections, Catch Basins, and Fittings | 7.2.5.3.(5) |
| CSA | CAN/CSA-A277–01 | Procedures for Certification of Factory-Built Houses | 9.1.1.9.(1) |
| CSA | CAN/CSA-A324-M88 | Clay Flue Liners | 9.21.3.3.(1) |
| CSA | A371-04 | Masonry Construction for Buildings | 5.6.1.3.(2) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.15.2.2.(3) |
|  |  |  | 9.20.3.2.(7) |
|  |  |  | 9.20.15.2.(1) |
| CSA | CAN/CSA-A405-M87 | Design and Construction of Masonry Chimneys and Fireplaces | 9.21.3.5.(1) |
|  |  |  | 9.22.1.4.(1) |
|  |  |  | 9.22.5.2.(2) |
| CSA | CAN/CSA-A438-00 | Concrete Construction for Housing and Small Buildings | 9.3.1.1.(1) |
| CSA | CAN/CSA-A440-00 | Windows | 5.10.1.1.(3) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.7.2.1.(1) |
|  |  |  | 9.7.2.1.(2) |
|  |  |  | 9.7.6.1.(1) |
| CSA | CAN/CSA-A440.1-00 | User Selection Guide to CSA Standard CAN/CSA-A440-00, Windows | 5.10.1.1.(3) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.7.2.1.(1) |
| CSA | CAN/CSA-A440.2-04 | Energy Performance Evaluation of Windows and Sliding Glass Doors | 12.3.1.3.(1) |
| CSA | A660-04 | Certification of Manufacturers of Steel Building Systems | 4.3.4.3.(1) |
| CSA | CAN/CSA-A3001-03 | Cementitious Materials for Use in Concrete | Table 5.10.1.1. |
|  |  |  | 9.3.1.2.(1) |
|  |  |  | 9.28.2.1.(1) |
| CSA | B44-00 | Safety Code for Elevators | 3.2.6.7.(2) |
|  |  |  | 3.5.2.1.(1) |
|  |  |  | 3.5.2.1.(2) |
|  |  |  | 3.5.2.1.(3) |
|  |  |  | 3.5.4.2.(1) |
|  |  |  | Table 4.1.5.12. |
|  |  |  | 7.4.3.6.(1) |
| CSA | CAN/CSA-B45.0-02 | General Requirements for Plumbing Fixtures | 7.6.4.2.(1) |
| CSA | CAN/CSA-B45.1-02 | Ceramic Plumbing Fixtures | 7.2.2.2.(2) |
| CSA | CAN/CSA-B45.2-02 | Enamelled Cast Iron Plumbing Fixtures | 7.2.2.2.(3) |
| CSA | CAN/CSA-B45.3-02 | Porcelain-Enamelled Steel Plumbing Fixtures | 7.2.2.2.(4) |
| CSA | CAN/CSA-B45.4-02 | Stainless Steel Plumbing Fixtures | 7.2.2.2.(5) |
| CSA | CAN/CSA-B45.5-02 | Plastic Plumbing Fixtures | 7.2.2.2.(6) |
| CSA | CAN/CSA-B45.9-02 | Macerating Systems and Related Components | 7.2.2.2.(8) |
| CSA | CAN/CSA-B45.10-01 | Hydromassage Bathtubs | 7.2.2.2.(7) |
| CSA | B52-99 | Mechanical Refrigeration Code | 6.2.2.4.(4) |
| CSA | CAN/CSA-B64.0-01 | Definitions, General Requirements, and Test Methods for Vacuum Breakers and Backflow Preventers | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.1.1-01 | Vacuum Breakers, Atmospheric Type (AVB) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.1.2-01 | Vacuum Breakers, Pressure Type (PVB) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.2-01 | Vacuum Breakers, Hose Connection Type (HCVB) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.2.1-01 | Vacuum Breakers, Hose Connection Type (HCVB) with Manual Draining Feature | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.2.2-01 | Vacuum Breakers, Hose Connection Type (HCVB) with Automatic Draining Feature | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.3-01 | Backflow Preventers, Dual Check Valve Type Atmospheric Port (DACP) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.4-01 | Backflow Preventers, Reduced Pressure Principle Type (RP) | 7.2.10.10.(1) |
|  |  |  | 7.6.2.3.(4) |
| CSA | CAN/CSA-B64.4.1-01 | Backflow Preventers, Reduced Pressure Principle Type for Fire Systems (RPF) | 7.6.2.4.(2); Table 7.6.2.4. |
|  |  |  | 7.6.2.4.(4) |
| CSA | CAN/CSA-B64.5-01 | Backflow Preventers, Double Check Valve Type (DCVA) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.5.1-01 | Backflow Preventers, Double Check Valve Type for Fire Systems (DCVAF) | 7.6.2.4.(2) |
|  |  |  | Table 7.6.2.4. |
| CSA | CAN/CSA-B64.6-01 | Backflow Preventers, Dual Check Valve Type (DuC) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.6.1-01 | Backflow Preventers, Dual Check Valve Type for Fire Systems (DuCF) | 7.6.2.4.(2) |
|  |  |  | Table 7.6.2.4. |
| CSA | CAN/CSA-B64.7-01 | Vacuum Breakers, Laboratory Faucet Type (LFVP) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.8-01 | Backflow Preventers, Dual Check Valve Type with Intermediate Vent (DuCV) | 7.2.10.10.(1) |
| CSA | CAN/CSA-B64.9-01 | Backflow Preventers, Single Check Valve Type for Fire Systems (SCVAF) | 7.6.2.4.(2) |
|  |  |  | Table 7.6.2.4. |
| CSA | CAN/CSA-B64.10-01 | Manual for the Selection and Installation of Backflow Prevention Devices | 7.2.10.10.(1) |
| CSA | B66-05 | Design, Material, and Manufacturing Requirements for Prefabricated Septic Tanks and Sewage Holding Tanks | 8.2.2.2.(1) |
|  |  |  | 8.2.2.2.(2) |
|  |  |  | 8.2.2.2.(3) |
|  |  |  | 8.2.2.3.(7) |
| CSA | CAN/CSA-B70-02 | Cast Iron Soil Pipe, Fittings and Means of Joining | 7.2.6.1.(1) |
|  |  |  | 7.4.6.4.(2) |
| CSA | B111-1974 | Wire Nails, Spikes and Staples | 9.23.3.1.(1) |
|  |  |  | 9.26.2.2.(1) |
|  |  |  | 9.29.5.6.(1) |
| CSA | CAN/CSA-B125-01 | Plumbing Fittings | 7.2.3.3.(1) |
|  |  |  | 7.2.10.6.(1) |
|  |  |  | 7.2.10.7.(1) |
|  |  |  | 7.2.10.7.(2) |
|  |  |  | 7.2.10.10.(2) |
| CSA | B127.1-99 | Asbestos Cement Drain, Waste and Vent Pipe and Pipe Fittings | 7.2.5.1.(1) |
|  |  |  | 7.2.6.2.(1) |
| CSA | B127.2-M1977 | Components for Use in Asbestos Cement Building Sewer Systems | 7.2.5.1.(2) |
|  |  |  | 7.2.6.2.(1) |
| CSA | CAN/CSA-B137.1-02 | Polyethylene Pipe, Tubing and Fittings for Cold Water Pressure Services | 7.2.5.5.(1) |
| CSA | CAN/CSA-B137.2-02 | PVC Injection-Moulded Gasketed Fittings for Pressure Applications | 7.2.5.8.(1) |
|  |  |  | 7.2.5.10.(1) |
|  |  |  | Table 7.2.11.2. |
| CSA | CAN/CSA-B137.3-02 | Rigid Polyvinyl Chloride (PVC) Pipe for Pressure Applications | 7.2.5.8.(1) |
|  |  |  | 7.2.5.10.(1) |
|  |  |  | Table 7.2.11.2. |
| CSA | CAN/CSA-B137.5-02 | Crosslinked Polyethylene (PEX) Tubing Systems for Pressure Applications | 7.2.5.7.(1) |
|  |  |  | Table 7.2.11.2. |
| CSA | CAN/CSA-B137.6-02 | CPVC Pipe, Tubing and Fittings for Hot and Cold Water Distribution Systems | 7.2.5.9.(1) |
|  |  |  | 7.2.5.9.(2) |
|  |  |  | Table 7.2.11.2. |
| CSA | CAN/CSA-B137.9-99 | Polyethylene/Aluminium/Polyethylene Composite Pressure Pipe Systems | 7.2.5.13.(1) |
|  |  |  | Table 7.2.11.2. |
| CSA | CAN/CSA-B137.10-02 | Crosslinked Polyethylene/Aluminum Crosslinked Polyethylene Composite Pressure Pipe Systems | 7.2.5.14.(1) |
|  |  |  | Table 7.2.11.2. |
| CSA | CAN/CSA-B137.11-02 | Polypropylene (PP-R) Pipe and Fittings for Pressure Applications | 7.2.5.15.(1) |
| CSA | B158.1-1976 | Cast Brass Solder Joint Drainage, Waste and Vent Fittings | 7.2.7.5.(1) |
|  |  |  | 7.2.10.1.(1) |
| CSA | CAN/CSA-B181.1-02 | ABS Drain, Waste, and Vent Pipe and Pipe Fittings | 7.2.5.10.(1) |
|  |  |  | 7.2.5.11.(1) |
|  |  |  | 7.2.5.12.(1) |
|  |  |  | 7.2.5.12.(2) |
|  |  |  | 7.2.10.1.(2) |
|  |  |  | 7.4.6.4.(2) |
| CSA | CAN/CSA-B181.2-02 | PVC Drain, Waste, and Vent Pipe and Pipe Fittings | 7.2.5.10.(1) |
|  |  |  | 7.2.5.11.(1) |
|  |  |  | 7.2.5.12.(1) |
|  |  |  | 7.2.5.12.(2) |
|  |  |  | 7.2.10.1.(3) |
| CSA | CAN/CSA-B181.3-02 | Polyolefin Laboratory Drainage Systems | 7.2.8.1.(1) |
| CSA | CAN/CSA-B182.1-02 | Plastic Drain and Sewer Pipe and Pipe Fittings | Table 5.10.1.1. |
|  |  |  | 7.2.5.10.(1) |
|  |  |  | 7.2.5.12.(2) |
|  |  |  | 7.4.6.4.(2) |
|  |  |  | 9.14.3.1.(1) |
| CSA | CAN/CSA-B182.2-02 | PVC Sewer Pipe and Fittings (PSM Type) | 7.2.5.10.(1) |
|  |  |  | 7.2.5.12.(2) |
| CSA | CAN/CSA-B182.4-02 | Profile (Ribbed) PVC Sewer Pipe and Fittings | 7.2.5.10.(1) |
| CSA | CAN/CSA-B182.6-02 | Profile Polyethylene Sewer Pipe and Fittings | 7.2.5.10.(1) |
| CSA | CAN/CSA-B182.7-02 | Multilayer PVC Sewer Pipe (PSM Type) Having Reprocessed-Recycled Content | 7.2.5.10.(1) |
| CSA | CAN/CSA-B214-01 | Installation Code for Hydronic Heating Systems | 6.2.1.4.(6) |
| CSA | B242-M1980 | Groove and Shoulder Type Mechanical Pipe Couplings | 7.2.10.4.(1) |
| CSA | CAN/CSA-B272-93 | Prefabricated Self-Sealing Vent Flashings | 7.2.10.14.(2) |
| CSA | CAN/CSA-B355-00 | Lifts for Persons with Physical Disabilities | 3.8.3.5.(1) |
| CSA | CAN/CSA-B356-00 | Water Pressure Reducing Valves for Domestic Water Supply Systems | 7.2.10.12.(1) |
| CSA | CAN/CSA-B365-01 | Installation Code for Solid-Fuel Burning Appliances and Equipment | 6.2.1.4.(1) |
|  |  |  | 9.21.1.3.(2) |
|  |  |  | 9.22.10.2.(1) |
|  |  |  | 9.33.1.2.(1) |
| CSA | CAN/CSA-B366.1-M91 | Solid Fuel-Fired Central Heating Appliances | 6.2.1.4.(2) |
| CSA | CAN/CSA-B602-99 | Mechanical Couplings for Drain, Waste, and Vent Pipe and Sewer Pipe | 7.2.5.3.(2) |
|  |  |  | 7.2.10.4.(2) |
| CSA | CAN/CSA-C22.2 | Test Methods for Electrical Wires and Cables | 3.1.4.3.(1) |
|  | No. 0.3-01 |  | 3.1.4.3.(2) |
|  |  |  | 3.1.5.18.(1) |
|  |  |  | 3.1.5.18.(2) |
|  |  |  | 3.1.5.21.(1) |
|  |  |  | 3.1.5.21.(2) |
|  |  |  | 3.6.4.3.(1) |
| CSA | C22.2 No.113-M1984 | Fans and Ventilators | 9.32.3.9.(5) |
| CSA | C22.2 No. 141-02 | Unit Equipment for Emergency Lighting | 3.2.7.4.(2) |
|  |  |  | 9.9.11.3.(6) |
| CSA | C22.2 No. 211.0-03 | General Requirements and Methods of Testing for Nonmetallic Conduit | 3.1.5.20.(1) |
| CSA | CAN/CSA-C22.3 No. 1-01 | Overhead Systems | 3.1.19.1.(2) |
| CSA | CAN/CSA-C88-M90 | Power Transformers and Reactors | 3.6.2.7.(10) |
| CSA | CAN/CSA-C260-M90 | Rating for the Performance of Residential Mechanical Ventilating Equipment | 9.32.3.9.(1) |
|  |  |  | 9.32.3.9.(2) |
|  |  |  | Table 9.32.3.9. |
| CSA | C282-05 | Emergency Electrical Power Supply for Buildings | 3.2.7.5.(1) |
| CSA | CAN/CSA-C439-00 | Rating the Performance of Heat/Energy-Recovery Ventilators | 6.2.1.6.(2) |
|  |  |  | 9.32.3.11.(2) |
| CSA | CAN/CSA-C448.1-02 | Design and Installation of Earth Energy Systems for Commercial and Institutional Buildings | 6.2.1.4.(4) |
| CSA | CAN/CSA-C448.2-02 | Design and Installation of Earth Energy Systems for Residential and Other Small Buildings | 6.2.1.4.(3) |
| CSA | CAN/CSA-F280-M90 | Determining the Required Capacity of Residential Space Heating and Cooling Appliances | 6.2.1.1.(1) |
| CSA | CAN/CSA-F326-M91 | Residential Mechanical Ventilation Systems | 6.2.1.1.(1) |
| CSA | CAN/CSA-F379.1-88 | Solar Domestic Hot Water Systems (Liquid to Liquid Heat Transfer) | 7.2.10.13.(1) |
| CSA | CAN/CSA-F383-87 | Installation Code for Solar Domestic Hot Water Systems | 7.6.1.13.(1) |
| CSA | CAN/CSA-G30.18-M92 | Billet Steel Bars for Concrete Reinforcement | 9.3.1.1.(4) |
|  |  |  | 9.40.1.3.(1) |
| CSA | CAN/CSA-G40.21-04 | Structural Quality Steel | 4.2.3.8.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.23.4.3.(2) |
| CSA | CAN/CSA-G164-M92 | Hot Dip Galvanising of Irregularly Shaped Articles | 4.4.4.1.(4) |
| CSA | G401-01 | Corrugated Steel Pipe Products | 7.2.6.8.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.14.3.1.(1) |
| CSA | O80 Series-97 | Wood Preservation | 3.1.4.4.(1) |
|  |  |  | 4.2.3.2.(1) |
|  |  |  | 4.2.3.2.(2) |
|  |  |  | Table 5.10.1.1. |
| CSA | O80.1-97 | Preservative Treatment of All Timber Products by Pressure Processes | Table 5.10.1.1. |
|  |  |  | 9.3.2.9.(5) |
| CSA | O80.2-97 | Preservative Treatment of Lumber, Timber, Bridge Ties and Mine Ties by Pressure Processes | 4.2.3.2.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.3.2.9.(5) |
| CSA | O80.3-97 | Preservative Treatment of Piles by Pressure Processes | 4.2.3.2.(1) |
| CSA | O80.9-97 | Preservative Treatment of Plywood by Pressure Processes | Table 5.10.1.1. |
|  |  |  | 9.3.2.9.(5) |
| CSA | O80.15-97 | Preservative Treatment of Wood for Building Foundation Systems, Basements and Crawl Spaces by Pressure Processes | 4.2.3.2.(1) |
|  |  |  | Table 5.10.1.1. |
|  |  |  | 9.3.2.9.(5) |
| CSA | O80.34-97 | Preservative Treatment of Lumber and Timbers with Borates for Use Out of Ground Contact and Continuously Protected from Liquid Water | Table 5.10.1.1. |
|  |  |  | 9.3.2.9.(5) |
|  |  |  | 9.3.2.9.(6) |
| CSA | CAN/CSA-O86-01 (Including Supplement CAN/CSA-O86S1-05) | Engineering Design in Wood | Table 4.1.8.9. |
|  |  |  | 4.3.1.1.(1) |
| CSA | O115-M1982 | Hardwood and Decorative Plywood | Table 5.10.1.1. |
|  |  |  | 9.27.9.1.(1) |
|  |  |  | 9.30.2.2.(1) |
| CSA | O118.1-97 | Western Cedars Shakes and Shingles | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
|  |  |  | 9.27.7.1.(1) |
| CSA | O118.2-M81 | Eastern White Cedar Shingles | Table 5.10.1.1. |
|  |  |  | 9.26.2.1.(1) |
|  |  |  | 9.27.7.1.(1) |
| CSA | O121-M1978 | Douglas Fir Plywood | Table 5.10.1.1. |
|  |  |  | 9.23.14.2.(1) |
|  |  |  | 9.23.15.2.(1) |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.27.9.1.(1) |
|  |  |  | 9.30.2.2.(1) |
|  |  |  | Table A-13 |
|  |  |  | Table A-14 |
|  |  |  | Table A-15 |
| CSA | CAN/CSA-O122-M89 | Structural Glued-Laminated Timber | Table A-11 |
|  |  |  | Table A-16 |
| CSA | CAN/CSA-O132.2 Series-90 | Wood Flush Doors | Table 5.10.1.1. |
|  |  |  | 9.6.5.1.(1) |
| CSA | O141-05 | Softwood Lumber | Table 5.10.1.1. |
|  |  |  | 9.3.2.6.(1) |
| CSA | O151-04 | Canadian Softwood Plywood | Table 5.10.1.1. |
|  |  |  | 9.23.14.2.(1) |
|  |  |  | 9.23.15.2.(1) |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.27.9.1.(1) |
|  |  |  | 9.30.2.2.(1) |
|  |  |  | Table A-13 |
|  |  |  | Table A-14 |
|  |  |  | Table A-15 |
| CSA | O153-M1980 | Poplar Plywood | Table 5.10.1.1. |
|  |  |  | 9.23.14.2.(1) |
|  |  |  | 9.23.15.2.(1) |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.27.9.1.(1) |
|  |  |  | 9.30.2.2.(1) |
| CSA | CAN/CSA-O177-M89 | Qualification Code for Manufacturers of Structural Glued-Laminated Timber | 4.3.1.2.(1) |
|  |  |  | Table A-11 |
|  |  |  | Table A-16 |
| CSA | CAN/CSA-O325.0-92 | Construction Sheathing | Table 5.10.1.1. |
|  |  |  | 9.23.14.2.(1) |
|  |  |  | 9.23.14.4.(2) |
|  |  |  | Table 9.23.14.5.B. |
|  |  |  | 9.23.15.2.(1) |
|  |  |  | 9.23.15.3.(2) |
|  |  |  | Table 9.23.15.7.B. |
|  |  |  | Table 9.23.16.2.B. |
|  |  |  | 9.29.9.1.(2) |
|  |  |  | 9.29.9.2.(5) |
|  |  |  | Table A-13 |
|  |  |  | Table A-14 |
|  |  |  | Table A-15 |
| CSA | O437.0-93 | OSB and Waferboard | Table 5.10.1.1. |
|  |  |  | 9.23.14.2.(1) |
|  |  |  | 9.23.14.4.(2) |
|  |  |  | 9.23.15.2.(1) |
|  |  |  | 9.23.15.3.(2) |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.27.11.1.(1) |
|  |  |  | 9.29.9.1.(2) |
|  |  |  | 9.30.2.2.(1) |
|  |  |  | Table A-13 |
|  |  |  | Table A-14 |
|  |  |  | Table A-15 |
| CSA | CAN/CSA-S16-01 (Including Supplement CAN/CSA-S16S1-05) | Limit States Design of Steel Structures | Table 4.1.8.9. |
|  |  |  | 4.3.4.1.(1) |
| CSA | S37-01 | Antennas, Towers and Antenna Supporting Structures | 4.1.1.4.(2) |
| CSA | CAN/CSA-S136-01 (Including Supplement CAN/CSA-S136S1-04) | North American Specifications for the Design of Cold Formed Steel Structural Members (using the Appendix B provisions applicable to Canada) | 4.3.4.2.(1) |
| CSA | CAN3-S157-M83 | Strength Design in Aluminum | 4.3.5.1.(1) |
| CSA | S304.1-04 | Design of Masonry Structures | Table 4.1.8.9. |
|  |  |  | 4.3.2.1.(1) |
| CSA | S307-M1980 | Load Test Procedure for Wood Roof Trusses for Houses and Small Buildings | 9.23.13.11.(5) |
| CSA | CAN3-S367-M81 | Air Supported Structures | 4.4.1.1.(1) |
| CSA | CAN/CSA-S406-92 | Construction of Preserved Wood Foundations | 9.13.2.8.(1) |
|  |  |  | 9.15.2.4.(1) |
|  |  |  | 9.16.5.1.(1) |
| CSA | CAN/CSA-S413-94 | Parking Structures | 4.4.2.1.(1) |
| CSA | S478-95 | Guideline on Durability in Buildings | 5.1.4.2.(3) |
| CSA | Z32-04 | Electrical Safety and Essential Electrical Systems in Health Care Facilities | 3.2.7.3.(4) |
|  |  |  | 3.2.7.6.(1) |
| CSA | CAN/CSA-Z91-M90 | Safety Code for Window Cleaning Operations | 4.4.4.1.(1) |
| CSA | CAN/CSA-Z240.2.1-92 | Structural Requirements for Mobile Homes | 9.1.1.9.(1) |
|  |  |  | 9.12.2.2.(6) |
|  |  |  | 9.15.1.3.(1) |
| CSA | CAN/CSA-Z240.3.1-92 | Plumbing Requirements for Mobile Homes | 9.1.1.9.(1) |
| CSA | CSA Z240.10.1-94 | Site Preparation, Foundation and Anchorage of Mobile Homes | 9.15.1.3.(1) |
|  |  |  | 9.23.6.3.(1) |
| CSA | CAN/CSA-Z241 Series-03 | Park Model Trailers | 9.39.1.1.(1) |
|  |  |  | 9.39.2.1.(1) |
| CSA | CAN/CSA-Z305.1-92 | Non-Flammable Medical Gas Piping Systems | 3.7.3.1.(1) |
| CSA | CAN/CSA-Z317.2-01 | Special Requirements for Heating, Ventilation and Air Conditioning (HVAC) Systems in Health Care Facilities | 6.2.1.1.(1) |
| CWC | 2004 | Engineering Guide for Wood Frame Construction | 9.4.1.1.(1) |
| DBR | Building Research Note No. 126, 1979 | Relation Between Thermal Resistance and Heat Storage in Building Enclosures | 12.3.3.8.(1) |
| DBR | Technical Paper No. 194, | Fire Endurance of Protected Steel Columns and Beams | Table 11.5.1.1.A. |
|  | May 1965 |  | Table 11.5.1.1.B. |
|  |  |  | Table 11.5.1.1.C. |
|  |  |  | Table 11.5.1.1.D/E. |
|  |  |  | Table 11.5.1.1.F. |
| DBR | Technical Paper No. 207, | Fire Endurance of Unit Masonry Walls | Table 11.5.1.1.A. |
|  | October 1965 |  | Table 11.5.1.1.B. |
|  |  |  | Table 11.5.1.1.C. |
|  |  |  | Table 11.5.1.1.D/E. |
|  |  |  | Table 11.5.1.1.F. |
| DBR | Technical Paper No. 222, | Fire Endurance of Light Framed and Miscellaneous Assemblies | Table 11.5.1.1.A. |
|  | June 1966 |  | Table 11.5.1.1.B. |
|  |  |  | Table 11.5.1.1.C. |
|  |  |  | Table 11.5.1.1.D/E. |
|  |  |  | Table 11.5.1.1.F. |
| FINA | 2005 | Rules and Regulations - FINA Facilities Rules 2005-2009 - FR5 Diving Facilities | 3.11.4.1.(17) |
| HI | 2005 | Hydronics Institute Manuals | 6.2.1.1.(1) |
| HRAI | 2005 | Digest | 6.2.1.1.(1) |
|  |  |  | 6.2.3.5.(1) |
|  |  |  | 6.2.4.3.(12) |
| HUD | Rehabilitation Guidelines No. 8 - 1980 | Guideline on Fire Ratings of Archaic Materials and Assemblies | Table 11.5.1.1.A. |
|  |  |  | Table 11.5.1.1.B. |
|  |  |  | Table 11.5.1.1.C. |
|  |  |  | Table 11.5.1.1.D/E. |
|  |  |  | Table 11.5.1.1.F. |
| HVI | HVI 915-2006 | Procedure for Loudness Rating of Residential Fan Products | 9.32.3.9.(2) |
|  |  |  | Table 9.32.3.9. |
| HVI | HVI 916-2005 | Airflow Test Procedure | 9.32.3.9.(1) |
| ISO | ISO 8201; 1987(E) | Acoustics - Audible Emergency Evacuation Signal | 3.2.4.18.(2) |
| MAH | Supplementary Standard SA-1, June, 2006 | Objectives and Functional Statements Attributed to the Acceptable Solutions | 1.2.1.1.(1) of Division A |
|  |  |  | 1.2.1.1.(2) of Division A |
| MAH | Supplementary Standard SB-1, June, 2006 | Climatic and Seismic Data | 5.2.1.1.(1) |
|  |  |  | 5.2.1.1.(2) |
|  |  |  | 9.4.1.1.(3) |
|  |  |  | 9.4.2.2.(1) |
|  |  |  | Table 9.25.1.2. |
|  |  |  | Table 9.32.3.10.A. |
|  |  |  | 9.33.3.2.(1) |
|  |  |  | Table 12.3.2.1. |
|  |  |  | Table 12.3.4.2.A. |
| MAH | Supplementary Standard SB-2, June, 2006 | Fire Performance Ratings | 3.1.5.23.(1); 3.1.7.1.(2) |
|  |  |  | 3.1.8.14.(2); 3.1.9.5.(1) |
|  |  |  | 3.1.9.5.(2); 3.1.12.1.(3) |
|  |  |  | 3.2.3.12.(1); 3.2.3.13.(4) |
|  |  |  | 3.13.2.1.(8); 3.13.3.5.(1) |
|  |  |  | 3.13.3.6.(2); 3.13.4.2.(7) |
|  |  |  | 9.10.3.1.(1); 9.10.3.2.(1) |
|  |  |  | 9.10.5.1.(4); 9.10.9.9.(1) |
|  |  |  | 9.10.13.14.(1) |
| MAH | Supplementary Standard SB-3, August 15, 2006 | Fire and Sound Resistance of Building Assemblies | 9.10.3.1.(1) 9.10.5.1.(4) |
|  |  |  | 9.11.2.1.(1) |
|  |  |  | 9.11.2.1.(2) |
| MAH | Supplementary Standard SB-4, June, 2006 | Measures for Fire Safety in High Buildings | 3.2.6.9.(3) |
|  |  |  | 3.2.6.10.(2) |
|  |  |  | 3.2.6.14.(1) |
| MAH | Supplementary Standard SB-5, June, 2006 | Approved Sewage Treatment Units | 8.6.2.2.(5) |
| MAH | Supplementary Standard SB-6, June, 2006 | Percolation Times and Soil Descriptions | 8.2.1.2.(2) |
| MAH | Supplementary Standard SB-7, June, 2006 | Construction Requirements for Guards | 9.8.8.2.(5) |
| MAH | Supplementary Standard SB-8, June, 2006 | Design, Construction and Installation of Anchorage Systems for Fixed Access Ladders | 3.6.1.5.(1) |
| MAH | Supplementary Standard SB-9, June, 2006 | Requirements for Soil Gas Control | 9.13.4.1.(1) |
|  |  |  | 9.13.4.2.(2) to (4) |
| MAH | Supplementary Standard SB-10, June, 2006 | Energy Efficiency Supplement | 12.2.1.1.(2) |
|  |  |  | 12.3.4.1.(1) |
|  |  |  | 12.3.4.4.(3) |
|  |  |  | 12.3.4.6.(1) |
|  |  |  | 12.3.4.7.(3) |
|  |  |  | 12.3.4.12.(1) |
| MAH | Supplementary Standard SB-11, June, 2006 | Construction of Farm Buildings | 1.3.1.2.(4) of Division A |
| MAH | Supplementary Standard SC-1, June, 2006 | Code of Conduct for Registered Code Agencies | 3.7.4.1.(2) of Division C |
| MOE | Guidelines 1985, with Subsequent Revision | Guidelines for the Design of Sanitary Sewage Works, Storm Sewers, Water Storage Facilities, Water Distribution Systems, Servicing in areas subject to adverse conditions, Water Supply for small residential development and seasonally operated water supply | 7.1.6.5.(1) |
| NFPA | 2005 Publication | National Fire Codes | 6.2.1.1.(1) |
| NFPA | 13-1999 | Installation of Sprinkler Systems | 3.2.4.8.(2); 3.2.4.16.(1) |
|  |  |  | 3.2.5.13.(1); 3.2.8.4.(7) |
|  |  |  | 3.3.2.12.(3); 3.15.1.1.(3) |
|  |  |  | 3.15.1.1.(4); 3.15.1.5.(2) |
|  |  |  | 3.15.1.6.(2); 3.15.2.1.(1) |
|  |  |  | 3.15.2.2.(1); 3.15.3.1.(1) |
| NFPA | 13D-2002 | Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes | 3.2.5.13.(3) |
| NFPA | 13R-2002 | Installation of Sprinkler Systems in Residential Occupancies up to and including Four Stories in Height | 3.2.5.13.(2) |
| NFPA | 14-2003 | Installation of Standpipe, Private Hydrants and Hose Systems | 3.2.9.2.(1) |
| NFPA | 20-2003 | Installation of Stationary Pumps for Fire Protection | 3.2.5.19.(1) |
| NFPA | 24-2002 | Installation of Fire Service Mains and Their Appurtenances | 7.2.11.1.(1) |
| NFPA | 80-1999 | Fire Doors and Windows | 3.1.8.5.(2) |
|  |  |  | 3.1.8.10.(2) |
|  |  |  | 3.1.8.12.(2) |
|  |  |  | 3.1.8.12.(3) |
|  |  |  | 3.1.8.14.(1) |
|  |  |  | 3.12.3.1.(2) |
|  |  |  | 9.10.13.1.(1) |
| NFPA | 82-2004 | Incinerators, Waste and Linen Handling Systems and Equipment | 6.2.6.1.(1) |
|  |  |  | 9.10.10.5.(2) |
| NFPA | 96-2001 | Ventilation Control and Fire Protection of Commercial Cooking Operations | 6.2.2.6.(1) |
| NFPA | 130-2003 | Fixed Guideway Transit and Passenger Rail Systems | 3.12.7.1.(1) |
| NFPA | 211-2003 | Chimneys, Fireplaces, Vents and Solid Fuel-Burning Appliances | 6.3.1.2.(2) |
|  |  |  | 6.3.1.3.(1) |
| NFPA | 214-2005 | Water-Cooling Towers | 6.2.3.14.(3) |
| NFPA | 701-2004 | Fire Tests for Flame Propagation of Textiles and Films | 3.14.1.6.(1) |
|  |  |  | 3.14.2.5.(1) |
| NLGA | 2004 | Standard Grading Rules for Canadian Lumber (Interpretation Included) | 1.4.1.2.(1) of Division A |
|  |  |  | 9.3.2.1.(1) |
|  |  |  | Table 9.3.2.1. |
|  |  |  | Tables A-1 to A-10 |
| NRCan | January 2005 | Energuide for New Houses: Administrative and Technical Procedures | 12.2.1.1.(3) |
|  |  |  | 12.2.1.2.(3) |
| NSF/ANSI | 46-2005 | Evaluation of Components and Devices Used in Wastewater Treatment Systems | 8.6.2.1.(2) |
| SMACNA | 1995, 2nd Ediiton | HVAC Duct Construction Standards - Metal and Flexible | 6.2.4.2.(3) |
|  |  |  | 12.3.4.5.(1) |
|  |  |  | 12.3.4.5.(2) |
| TC |  | Canadian Aviation Regulations - Part III | 4.1.5.14. |
| TPIC | 1996 | Truss Design Procedures and Specifications for Light Metal Plate Connected Wood Trusses | 9.23.13.11.(6) |
| UL | UL 300-2005 | Fire Extinguishing Systems for Protection of Restaurant Cooking Areas | 6.2.2.6.(2) |
| UL | UL 2034-1996 | Single and Multiple Station Carbon Monoxide Alarms | 6.2.3.12.(1) |
|  |  |  | 9.33.4.3.(1) |
| ULC | CAN/ULC-S101-04 | Fire Endurance Tests of Building Construction and Materials | 3.1.5.12.(3) |
|  |  |  | 3.1.5.12.(4) |
|  |  |  | 3.1.5.12.(6) |
|  |  |  | 3.1.7.1.(1) |
|  |  |  | 3.1.11.7.(1) |
|  |  |  | 3.2.3.8.(1) |
|  |  |  | 3.2.6.9.(6) |
| ULC | CAN/ULC-S102-03 | Test for Surface Burning Characteristics of Building Materials and Assemblies | 3.1.5.25.(1) |
|  |  |  | 3.1.12.1.(1) |
| ULC | CAN/ULC-S102.2-03 | Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies | 3.1.12.1.(2) |
|  |  |  | 3.1.13.4.(1) |
| ULC | S102.3-M82 | Fire Test of Light Diffusers and Lenses | 3.1.13.4.(1) |
| ULC | CAN4-S104-M80 | Fire Tests of Door Assemblies | 3.1.8.4.(1) |
|  |  |  | 3.2.6.9.(3) |
| ULC | CAN4-S105-M85 | Fire Door Frames Meeting the Performance Required by CAN4-S104 | 9.10.13.6.(1) |
| ULC | CAN4-S106-M80 | Fire Tests of Window and Glass Block Assemblies | 3.1.8.4.(1) |
| ULC | CAN/ULC-S107-03 | Fire Tests of Roof Coverings | 3.1.15.1.(1) |
| ULC | CAN/ULC-S109-03 | Flame Tests of Flame-Resistant Fabrics and Films | 3.1.16.1.(1) |
|  |  |  | 3.14.1.6.(1) |
|  |  |  | 3.14.2.5.(1) |
|  |  |  | 6.2.3.17.(1) |
|  |  |  | 6.2.3.18.(1) |
|  |  |  | 6.2.4.9.(1) |
| ULC | CAN/ULC-S110-M86 | Tests for Air Ducts | 6.2.3.2.(2) |
|  |  |  | 6.2.3.2.(4) |
| ULC | ULC-S111-95 | Fire Tests for Air Filter Units | 6.2.3.13.(1) |
|  |  |  | 6.2.4.14.(1) |
| ULC | CAN/ULC-S112-M90 | Fire Test of Fire-Damper Assemblies | 3.1.8.4.(1) |
| ULC | CAN/ULC-S112.1-M90 | Leakage Rated Dampers for Use in Smoke Control Systems | 6.2.3.9.(3) |
| ULC | CAN4-S112.2-M84 | Fire Test of Ceiling Firestop Flap Assemblies | 3.1.9.5.(2) |
|  |  |  | 3.6.4.3.(2) |
| ULC | CAN4-S113-79 | Wood Core Doors Meeting the Performance Required by CAN4-S104-77 for Twenty Minute Fire Rated Closure Assemblies | 9.10.13.2.(1) |
| ULC | CAN4-S114-M80 | Test for Determination of Non-Combustibility in Building Materials | 1.4.1.2.(1) of Division A |
| ULC | ULC-S115-95 | Fire Tests of Firestop Systems | 3.1.5.16.(3) |
|  |  |  | 3.1.9.1.(1) |
|  |  |  | 3.1.9.1.(2) |
|  |  |  | 3.1.9.4.(4) |
|  |  |  | 9.10.9.7.(3) |
| ULC | CAN4-S124-M85 | Test for the Evaluation of Protective Coverings for Foamed Plastic | 3.1.5.12.(2) |
| ULC | CAN/ULC-S126-M86 | Test for Fire Spread Under Roof-Deck Assemblies | 3.1.14.1.(1) |
|  |  |  | 3.1.14.2.(1) |
| ULC | CAN/ULC-S134-92 | Fire Test of Exterior Wall Assemblies | 3.1.5.5.(1) |
| ULC | CAN/ULC-S135-04 | Test Method for the Determination of Combustibility Parameters of Building Materials Using an Oxygen Consumption Calorimeter (Cone Calorimeter) | 3.1.5.1.(2) |
| ULC | ULC-S139-00 | Fire Test for Evaluation of Integrity of Electrical Cables | 3.2.7.10.(2) |
| ULC | S505-1974 | Fusible Links for Fire Protection Service | 3.1.8.9.(1) |
| ULC | S513-1978 | Threaded Couplings for 38 mm and 65 mm Fire Hose | 3.2.9.2.(7) |
| ULC | CAN/ULC-S524-01 | Installation of Fire Alarm Systems | 3.2.4.5.(1) |
| ULC | CAN/ULC-S531-02 | Smoke Alarms | 3.2.4.21.(1) |
|  |  |  | 9.10.19.1.(1) |
| ULC | CAN/ULC-S537-04 | Verification of Fire Alarm Systems | 3.2.4.5.(2) |
| ULC | S543-M84 | Internal Lug Quick Connect Couplings for Fire Hoses | 3.2.9.2.(7) |
| ULC | CAN/ULC-S553-02 | Installation of Smoke Alarms | 3.2.4.21.(7) |
| ULC | CAN/ULC-S561-03 | Installation and Services for Fire Signal Receiving Centres and Systems | 3.2.4.7.(4) |
| ULC | CAN/ULC-S610-M87 | Factory-Built Fireplaces | 9.22.8.1.(1) |
| ULC | ULC-S628-93 | Fireplace Inserts | 9.22.10.1.(1) |
| ULC | CAN/ULC-S629-M87 | 650ºC Factory-Built Chimneys | 9.21.1.2.(1) |
| ULC | CAN/ULC-S639-M87 | Steel Liner Assemblies for Solid Fuel-Burning Masonry Fireplaces | 9.22.2.3.(1) |
| ULC | CAN/ULC-S701-01 | Thermal Insulation, Polystyrene, Boards and Pipe Covering | Table 5.10.1.1. |
|  |  |  | 9.15.4.1.(1) |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.25.2.2.(1) |
|  |  |  | 9.25.2.2.(4) |
| ULC | CAN/ULC-S702-97 | Mineral Fibre Thermal Insulation for Buildings | Table 5.10.1.1. |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.25.2.2.(1) |
| ULC | CAN/ULC-S703-01 | Cellulose Fibre Insulation (CFI) for Buildings | Table 5.10.1.1. |
|  |  |  | 9.25.2.2.(1) |
| ULC | CAN/ULC-S704-03 | Thermal Insulation, Polyurethane and Polyisocyanurate Boards, Faced | Table 5.10.1.1. |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.25.2.2.(1) |
| ULC | CAN/ULC-S705.1-01 | Thermal Insulation - Spray Applied Rigid Polyurethane Foam, Medium Density - Material Specification | Table 5.10.1.1. |
|  |  |  | 9.25.2.2.(1) |
| ULC | CAN/ULC-S705.2-98 | Thermal Insulation - Spray Applied Rigid Polyurethane Foam, Medium Density, Installers’s Responsibilities - Specification | Table 5.10.1.1. |
|  |  |  | 9.25.2.2.(1) |
|  |  |  | 9.25.2.5.(1) |
| ULC | CAN/ULC-S706-02 | Wood Fibre Thermal Insulation for Buildings | Table 5.10.1.1. |
|  |  |  | 9.23.15.7.(3) |
|  |  |  | Table 9.23.16.2.A. |
|  |  |  | 9.25.2.2.(1) |
|  |  |  | 9.29.8.1.(1) |
| ULC | ULC/ORD-C263.1-99 | Sprinkler-Protected Window Systems | 3.1.8.18.(1) |
| ULC | ULC/ORD-C199P-02 | Combustible Piping for Sprinkler Systems | 3.2.5.14.(2) |
|  |  |  | 3.2.5.14.(5) |
| ULC | ULC/ORD-C376-1995 | Fire Growth of Foamed Plastic Insulated Building Panels in a Full-Scale Room Configuration | 3.1.5.12.(7) |
| ULC | ULC/ORD-C1254.6-1995 | Fire Testing of Restaurant Cooking Area Fire Extinguishing System Units | 6.2.2.6.(2) |

1.3.2.  Abbreviations

1.3.2.1.  Abbreviations of Proper Names

(1)  In this Code, an abbreviation of proper names listed in Column 1 of Table 1.3.2.1. shall have the meaning assigned opposite it in Column 2.

TABLE 1.3.2.1.
ABBREVIATIONS OF PROPER NAMES

| Column 1 | Column 2 |
| --- | --- |
| Abbreviation | Meaning |
| ACGIH | American Conference of Governmental Industrial Hygienists |
| ANSI | American National Standards Institute |
| APHA | American Public Health Association |
| ASHRAE | American Society of Heating, Refrigerating and Air-Conditioning Engineers |
| ASME | The American Society of Mechanical Engineers |
| ASSE | American Society of Sanitary Engineering |
| ASTM | American Society for Testing and Materials |
| AWPA | American Wood-Preservers’ Association |
| AWWA | American Water Works Association |
| BNQ | Bureau de Normalisation du Québec |
| CAN | National Standard of Canada designation |
|  | The number or name following the CAN designation represents the agency under whose auspices the standard is issued. |
|  | CAN1 designates CGA, |
|  | CAN2 designates CGSB, |
|  | CAN3 designates CSA, and |
|  | CAN4 designates ULC. |
| CCBFC | Canadian Commission on Building and Fire Codes |
| CGSB | Canadian General Standards Board |
| CSA | Canadian Standards Association |
| CWC | Canadian Wood Council |
| DBR | Division of Building Research, known as the Institute for Research in Construction since 1985 |
| FINA | Fédération Internationale de Natation Amateur |
| HI | Hydronics Institute |
| HRAI | Heating, Refrigerating and Air-Conditioning Institute of Canada |
| HVI | Home Ventilating Institute |
| IESNA | Illuminating Engineering Society of North America |
| ISO | International Organization for Standardization |
| HUD | U.S. Department of Housing and Urban Development |
| MAH | Ontario Ministry of Municipal Affairs and Housing |
| MOE | Ontario Ministry of the Environment |
| NFPA | National Fire Protection Association |
| NLGA | National Lumber Grades Authority |
| NRCan | Natural Resources Canada |
| NSF | NSF International, formerly called National Sanitation Federation |
| SMACNA | Sheet Metal and Air Conditioning Contractors National Association Inc. |
| TC | Transport Canada |
| TPIC | Truss Plate Institute of Canada |
| UL | Underwriters Laboratories Inc. |
| ULC | Underwriters’ Laboratories of Canada |
| WEF | World Environment Federation |

O. Reg. 350/06, Division B, Part 1; O. Reg. 137/07, s. 7.

Part 2

(Reserved)

Part 3
Fire Protection, Occupant Safety and Accessibility

| Section | 3.1. | General |
| --- | --- | --- |
|  | 3.1.1. | Scope |
|  | 3.1.2. | Classification of Buildings or Parts of Buildings by Major Occupancy |
|  | 3.1.3. | Multiple Occupancy Requirements |
|  | 3.1.4. | Combustible Construction |
|  | 3.1.5. | Noncombustible Construction |
|  | 3.1.6. | Reserved |
|  | 3.1.7. | Fire-Resistance Ratings |
|  | 3.1.8. | Fire Separations and Closures |
|  | 3.1.9. | Building Services in Fire Separations and Fire Rated Assemblies |
|  | 3.1.10. | Firewalls |
|  | 3.1.11. | Fire Stops in Concealed Spaces |
|  | 3.1.12. | Flame-Spread Rating and Smoke Developed Classification |
|  | 3.1.13. | Interior Finish |
|  | 3.1.14. | Roof Assemblies |
|  | 3.1.15. | Roof Covering |
|  | 3.1.16. | Fabrics |
|  | 3.1.17. | Occupant Load |
|  | 3.1.18. | Drainage and Grades |
|  | 3.1.19. | Above Ground Electrical Conductors |
| Section | 3.2. | Building Fire Safety |
|  | 3.2.1. | General |
|  | 3.2.2. | Building Size and Construction Relative to Occupancy |
|  | 3.2.3. | Spatial Separation and Exposure Protection |
|  | 3.2.4. | Fire Alarm and Detection Systems |
|  | 3.2.5. | Provisions for Fire Fighting |
|  | 3.2.6. | Additional Requirements for High Buildings |
|  | 3.2.7. | Lighting and Emergency Power Systems |
|  | 3.2.8. | Mezzanines and Openings Through Floor Assemblies |
|  | 3.2.9. | Standpipe Systems |
| Section | 3.3. | Safety Within Floor Areas |
|  | 3.3.1. | All Floor Areas |
|  | 3.3.2. | Assembly Occupancy |
|  | 3.3.3. | Care or Detention Occupancy |
|  | 3.3.4. | Residential Occupancy |
|  | 3.3.5. | Industrial Occupancy |
| Section | 3.4. | Exits |
|  | 3.4.1. | General |
|  | 3.4.2. | Number and Location of Exits from Floor Areas |
|  | 3.4.3. | Width and Height of Exits |
|  | 3.4.4. | Fire Separation of Exits |
|  | 3.4.5. | Exit Signs |
|  | 3.4.6. | Types of Exit Facilities |
|  | 3.4.7. | Fire Escapes |
| Section | 3.5. | Vertical Transportation |
|  | 3.5.1. | General |
|  | 3.5.2. | Elevator Requirements |
|  | 3.5.3. | Fire Separations |
|  | 3.5.4. | Dimensions and Signs |
| Section | 3.6. | Service Facilities |
|  | 3.6.1. | General |
|  | 3.6.2. | Service Rooms |
|  | 3.6.3. | Vertical Service Spaces and Service Facilities |
|  | 3.6.4. | Horizontal Service Spaces and Service Facilities |
| Section | 3.7. | Health Requirements |
|  | 3.7.1. | Height and Area of Rooms |
|  | 3.7.2. | Windows |
|  | 3.7.3. | Reserved |
|  | 3.7.4. | Plumbing Facilities |
|  | 3.7.5. | Health Care Facility Systems |
|  | 3.7.6. | Food Premises |
| Section | 3.8. | Barrier-Free Design |
|  | 3.8.1. | General |
|  | 3.8.2. | Occupancy Requirements |
|  | 3.8.3. | Design Standards |
| Section | 3.9. | Portable Classrooms |
|  | 3.9.1. | Scope |
|  | 3.9.2. | Interior Finish |
|  | 3.9.3. | Application |
| Section | 3.10. | Self-Service Storage Buildings |
|  | 3.10.1. | Scope |
|  | 3.10.2. | Requirements for All Buildings |
|  | 3.10.3. | Additional Requirements for Buildings Containing more than 1 Storey |
|  | 3.10.4. | Additional Requirements for 1 Storey Buildings |
| Section | 3.11. | Public Pools |
|  | 3.11.1. | General |
|  | 3.11.2. | Designations of Public Pools |
|  | 3.11.3. | Pool and Pool Deck Design and Construction Requirements for All Class A and Class B Pools |
|  | 3.11.4. | Public Pools Equipped with Diving Boards or Diving Platforms |
|  | 3.11.5. | Ramps into Public Pools in Group B, Division 2 or 3, Major Occupancies |
|  | 3.11.6. | Modified Pools |
|  | 3.11.7. | Wave Action Pools |
|  | 3.11.8. | Recirculation for Public Pools |
|  | 3.11.9. | Dressing Rooms, Locker Facilities and Plumbing Facilities for All Public Pools |
|  | 3.11.10. | Emergency Provisions for All Public Pools |
|  | 3.11.11. | Service Rooms and Storage for All Public Pools |
| Section | 3.12. | Public Spas |
|  | 3.12.1. | General |
|  | 3.12.2. | Public Spa and Deck Design and Construction Requirements |
|  | 3.12.3. | Ramps into Public Spas |
|  | 3.12.4. | Water Circulation for Public Spas |
|  | 3.12.5. | Emergency Provisions for All Public Spas |
|  | 3.12.6. | Service Rooms and Storage for All Public Spas |
| Section | 3.13. | Rapid Transit Stations |
|  | 3.13.1. | Scope and Definitions |
|  | 3.13.2. | Construction Requirements |
|  | 3.13.3. | Safety Requirements Within Stations |
|  | 3.13.4. | Means of Egress |
|  | 3.13 5. | Fire Safety Provisions |
|  | 3.13.6. | Required Sanitary Facilities |
|  | 3.13.7. | Emergency Ventilation |
|  | 3.13.8. | Barrier-Free Design |
| Section | 3.14. | Tents and Air-Supported Structures |
|  | 3.14.1. | Tents |
|  | 3.14.2. | Air-Supported Structures |
| Section | 3.15. | Signs |
|  | 3.15.1. | Scope |
|  | 3.15.2. | Alterations |
|  | 3.15.3 | Structural Requirements |
|  | 3.15.4. | Plastic Sign Facing Materials |
|  | 3.15.5 | Location Restrictions |
| Section | 3.16. | Shelf and Rack Storage Systems |
|  | 3.16.1. | Scope |
|  | 3.16.2. | Storage of Class I, II, III and IV Commodities |
|  | 3.16.3. | Storage of Group A, B and C Plastics and Rubber Tires |
| Section | 3.17. | Additional Requirements For Change of Use |
|  | 3.17.1. | Scope |
|  | 3.17.2. | Additional Construction |

Section 3.1.  General

3.1.1.  Scope

3.1.1.1.  Scope

(1)  The scope of this Part shall be as described in Subsection 1.1.2. of Division A.

3.1.1.2.  Reserved

3.1.1.3.  Radon

(1)  In addition to all other requirements, a building in the following designated areas shall be designed and constructed so that the annual average concentration of radon 222 does not exceed 250 millibecquerels per litre of air and the annual average concentration of the short lived daughters of radon 222 does not exceed 0.02 working levels inside the building:

(a)	The Town of Elliot Lake in the Territorial District of Algoma,

(b)	The Township of Faraday in the County of Hastings, and

(c)	The geographic Township of Hyman in the Territorial District of Sudbury.

3.1.1.4.  Building in Flood Plains

(1)  Buildings constructed on flood plains shall,

(a)	be designed and constructed in accordance with good engineering practice to withstand anticipated vertical and horizontal hydrostatic pressures acting on the structure, and

(b)	incorporate floodproofing measures that will preserve the integrity of exits and means of egress during times of flooding.

3.1.2.  Classification of Buildings or Parts of Buildings by Major Occupancy

3.1.2.1.  Classification of Buildings

(1)  Except as permitted by Articles 3.1.2.3. to 3.1.2.6., every building or part of it shall be classified according to its major occupancy as belonging to one of the Groups or Divisions described in Table 3.1.2.1.

(2)  A building intended for use by more than one major occupancy shall be classified according to all major occupancies for which it is used or intended to be used.

3.1.2.2.  Occupancies of the Same Classification

(1)  Any building is deemed to be occupied by a single major occupancy, notwithstanding its use for more than one major occupancy, provided that all occupancies are classified as belonging to the same Group classification or, where the Group is divided into Divisions, as belonging to the same Division classification described in Table 3.1.2.1.

Table 3.1.2.1.
Major Occupancy Classification

Forming Part of Sentence 3.1.2.1.(1)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Group | Division | Description of Major Occupancies |
| A | 1 | Assembly occupancies intended for the production and viewing of the performing arts |
| A | 2 | Assembly occupancies not elsewhere classified in Group A |
| A | 3 | Assembly occupancies of the arena type |
| A | 4 | Assembly occupancies in which occupants are gathered in the open air |
| B | 1 | Detention occupancies |
| B | 2 | Care and treatment occupancies |
| B | 3 | Care occupancies |
| C | --- | Residential occupancies |
| D | --- | Business and personal services occupancies |
| E | --- | Mercantile occupancies |
| F | 1 | High hazard industrial occupancies |
| F | 2 | Medium hazard industrial occupancies |
| F | 3 | Low hazard industrial occupancies |

3.1.2.3.  Arena Type Buildings

(1)  An arena type building intended for occasional use for trade shows and similar exhibition purposes shall be classified as Group A, Division 3 occupancy.

3.1.2.4.  Police Stations

(1)  A police station with detention quarters is permitted to be classified as a Group B, Division 2 major occupancy provided the station is not more than 1 storey in building height and 600 m2 in building area.

3.1.2.5.  Group B, Division 3 Occupancies

(1)  Group B, Division 3 occupancies are permitted to be classified as Group C major occupancies provided,

(a)	the occupants live as a single housekeeping unit in a suite with sleeping accommodation for not more than 10 persons, and

(b)	not more than 2 occupants require assistance in evacuation in case of an emergency.

3.1.2.6.  Restaurants

(1)  A restaurant is permitted to be classified as a Group E major occupancy provided the restaurant is designed to accommodate not more than 30 persons consuming food or drink.

3.1.3.  Multiple Occupancy Requirements

3.1.3.1.  Separation of Major Occupancies

(1)  Except as permitted by Sentences (2) and (3), major occupancies shall be separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Table 3.1.3.1.

Table 3.1.3.1.
Major Occupancy Fire Separations(1)

Forming Part of Sentence 3.1.3.1.(1)

| Column 1 | Col. 2 | Col. 3 | Col. 4 | Col. 5 | Col. 6 | Col. 7 | Col. 8 | Col. 9 | Col. 10 | Col. 11 | Col. 12 | Col. 13 | Col. 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Major Occupancy | Minimum Fire-Resistance Rating of Fire Separation, h (1) |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Adjoining Major Occupancy |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A-1 | A-2 | A-3 | A-4 | B-1 | B-2 | B-3 | C | D | E | F-1 | F-2 | F-3 |
| A-1 | --- | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 2 | (2) | 2 | 1 |
| A-2 | 1 | --- | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 2 | (2) | 2 | 1 |
| A-3 | 1 | 1 | --- | 1 | 2 | 2 | 2 | 1 | 1 | 2 | (2) | 2 | 1 |
| A-4 | 1 | 1 | 1 | --- | 2 | 2 | 2 | 1 | 1 | 2 | (2) | 2 | 1 |
| B-1 | 2 | 2 | 2 | 2 | --- | 2 | 2 | 2 | 2 | 2 | (2) | 2 | 2 |
| B-2 | 2 | 2 | 2 | 2 | 2 | --- | 1 | 2 | 2 | 2 | (2) | 2 | 2 |
| B-3 | 2 | 2 | 2 | 2 | 2 | 1 | --- | 2 | 2 | 2 | (2) | 2 | 2 |
| C | 1 | 1 | 1 | 1 | 2 | 2 | 2 | --- | 1 | 2(3) | (2) | 2(4) | 1 |
| D | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | --- | --- | 3 | --- | --- |
| E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2(3) | --- | --- | 3 | --- | --- |
| F-1 | (2) | (2) | (2) | (2) | (2) | (2) | (2) | (2) | 3 | 3 | --- | 2 | 2 |
| F-2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2(4) | --- | --- | 2 | --- | --- |
| F-3 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | --- | --- | 2 | --- | --- |

Notes to Table 3.1.3.1.:

(1) Section 3.3. contains requirements for the separation of occupancies and tenancies that are in addition to the requirements for the separation of major occupancies.

(2) See Sentence 3.1.3.2.(1).

(3) See Sentence 3.1.3.1.(2).

(4) See Sentence 3.1.3.2.(2).

(2)  In a building not more than 3 storeys in building height, if not more than 2 dwelling units are contained together with a Group E major occupancy, the fire-resistance rating of the fire separation between the 2 major occupancies need not be more than 1 h.

(3)  The fire separations required between major occupancies in Sentence (1) are permitted to be penetrated by floor openings protected in conformance with Subsection 3.2.8., except for fire separations for Group F, Division 1 major occupancies and for mezzanines described in Sentence 3.2.8.2.(1).

3.1.3.2.  Prohibition of Occupancy Combinations

(1)  No major occupancy of Group F, Division 1 shall be contained within a building with any occupancy classified as Group A, B or C.

(2)  Except as provided in Sentence (4) and Sentence 3.10.2.4.(9), not more than one suite of residential occupancy shall be contained within a building classified as a Group F, Division 2 major occupancy.

(3)  A sleeping room or sleeping area shall not open directly into a room or area where food is intended to be stored, prepared, processed, distributed, served, sold or offered for sale.

(4)  A Group F, Division 2 major occupancy is permitted in a building containing only live/work units and is for the exclusive use of the occupants of the live/work units.

3.1.4.  Combustible Construction

3.1.4.1.  Combustible Materials Permitted

(1)  A building permitted to be of combustible construction is permitted to be constructed of combustible materials, with or without noncombustible components.

3.1.4.2.  Protection of Foamed Plastics

(1)  Foamed plastics that form part of a wall or ceiling assembly in combustible construction shall be protected from adjacent spaces in the building, other than adjacent concealed spaces within attic or roof spaces, crawl spaces, and wall assemblies,

(a)	by one of the interior finishes described in Subsections 9.29.4. to 9.29.9.,

(b)	by any thermal barrier that meets the requirements of Sentence 3.1.5.12.(2), or

(c)	where the building does not contain a Group B or Group C major occupancy, by sheet metal,

(i)	mechanically fastened to the supporting assembly independent of the insulation,

(ii)	not less than 0.38 mm thick, and

(iii)	with a melting point not below 650°C.

(2)  The flame-spread rating on any exposed surface of combustible insulation, or any surface that would be exposed by cutting through it in any direction, shall be not more than 500.

3.1.4.3.  Wires and Cables

(1)  Optical fibre cables and electrical wires and cables installed in a building permitted to be of combustible construction shall,

(a)	not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test in Clause 4.11.1. of CAN/CSA-C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables”, or

(b)	be located in,

(i)	totally enclosed noncombustible raceways,

(ii)	concealed spaces in walls,

(iii)	concrete slabs, or

(iv)	totally enclosed nonmetallic raceways conforming to Article 3.1.5.20.

(2)  The requirement in Clause (1)(a) is considered to be met where the wires and cables,

(a)	exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating), or

(b)	exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating).

(3)  Service-entrance cables for communication and community antennae distribution systems need not conform to Sentence (1) provided,

(a)	the service-entrance cables are located in a building permitted to be of combustible construction and are not more than 3 m in length from the point of entry into the building or from the point of leaving protection as required in Clause (1)(b), or

(b)	the service entrance cables enter into an electrical or telephone service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

3.1.4.4.  Fire-Retardant Treated Wood

(1)  If fire-retardant treated wood is specified in this Part, the wood shall,

(a)	be pressure impregnated with fire-retardant chemicals in conformance with CAN/CSA-O80 Series-M, “Wood Preservation”, and

(b)	have a flame-spread rating not more than 25.

3.1.4.5.  Heavy Timber Construction Alternative

(1)  If combustible construction is permitted and is not required to have a fire-resistance rating more than 45 min, heavy timber construction is permitted to be used.

(2)  If heavy timber construction is permitted, it shall conform to Article 3.1.4.6.

3.1.4.6.  Heavy Timber Construction

(1)  Wood elements in heavy timber construction shall be arranged in heavy solid masses and with essentially smooth flat surfaces to avoid thin sections and sharp projections.

(2)  Except as permitted by Sentences (3) to (6) and (12), the minimum dimensions of wood elements in heavy timber construction shall conform to Table 3.1.4.6.

Table 3.1.4.6.
Heavy Timber Dimensions

Forming Part of Sentence 3.1.4.6.(3)

| Column 1 | Column 2 | Column 3 | Column 4 | Column 5 |
| --- | --- | --- | --- | --- |
| Supported Assembly | Structural Element | Solid Sawn (width × depth), mm × mm | Glued-Laminated (width × depth), mm × mm | Round (diam), mm |
| Roofs only | Columns | 140 × 191 | 130 × 190 | 180 |
|  | Arches supported on the tops of walls or abutments | 89 × 140 | 80 × 152 | --- |
|  | Beams, girders and trusses | 89 × 140 | 80 × 152 | --- |
|  | Arches supported at or near the floor line | 140 × 140 | 130 × 152 | --- |
| Floors, floors plus roofs | Columns | 191 × 191 | 175 × 190 | 200 |
|  | Beams, girders, trusses and arches | 140 × 241 or 191 × 191 | 130 × 228 or175 × 190 | --- |

(3)  Where splice plates are used at splices of roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction shall be not less than 64 mm thick.

(4)  Floors in heavy timber construction shall be of glued-laminated or solid sawn plank not less than,

(a)	64 mm thick, splined or tongued and grooved, or

(b)	38 mm wide and 89 mm deep set on edge and well-spiked together.

(5)  Floors in heavy timber construction shall be laid,

(a)	so that no continuous line of end joints will occur except at points of support, and covered with,

(i)	tongued and grooved flooring not less than 19 mm thick laid cross-wise or diagonally, or

(ii)	tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 12.5 mm thick, and

(b)	not closer than 15 mm to the walls to provide for expansion, with the gap covered at the top or bottom.

(6)  Roofs in heavy timber construction shall be of tongued and grooved phenolic-bonded plywood not less than 28 mm thick, or glued-laminated or solid sawn plank that is,

(a)	not less than 38 mm thick, splined or tongued and grooved, or

(b)	not less than 38 mm wide and 64 mm deep set on edge and laid so that no continuous line of end joints will occur except at the points of support.

(7)  Wood columns in heavy timber construction shall be continuous or superimposed throughout all storeys.

(8)  Superimposed wood columns in heavy timber construction shall be connected by,

(a)	reinforced concrete or metal caps with brackets,

(b)	steel or iron caps with pintles and base plates, or

(c)	timber splice plates fastened to the columns by metal connectors housed within the contact faces.

(9)  Where beams and girders in heavy timber construction enter masonry, wall plates, boxes of the self-releasing type or hangers shall be used.

(10)  Wood girders and beams in heavy timber construction shall be closely fitted to columns, and adjoining ends shall be connected by ties or caps to transfer horizontal loads across the joints.

(11)  In heavy timber construction, intermediate wood beams used to support a floor shall be supported on top of the girders or on metal hangers into which the ends of the beams are closely fitted.

(12)  Roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction are permitted to be not less than 64 mm wide provided,

(a)	where two or more spaced members are used, the intervening spaces are,

(i)	blocked solidly throughout, or

(ii)	tightly closed by a continuous wood cover plate not less than 38 mm thick secured to the underside of the members, or

(b)	the space below the roof deck or sheathing is sprinklered.

3.1.5.  Noncombustible Construction

3.1.5.1.  Noncombustible Materials

(1)  Except as permitted by Sentences (2) to (4) and Articles 3.1.5.2. to 3.1.5.25., 3.1.13.4. and 3.2.2.16., a building or part of a building required to be of noncombustible construction, shall be constructed with noncombustible materials.

(2)  Notwithstanding the definition for noncombustible materials stated in Article 1.4.1.2. of Division A, a material is permitted to be used in noncombustible construction provided that, when tested in accordance with CAN/ULC-S135, “Test Method for the Determination of Combustibility Parameters of Building Materials Using an Oxygen Consumption Calorimeter (Cone Calorimeter)” at a heat flux of 50 kW/m2,

(a)	its average total heat release is not more than 3 MJ/m2,

(b)	its average total smoke extinction area is not more than 1.0 m2, and

(c)	the test duration is extended beyond the time stipulated in the referenced standard until it is clear that there is no further release of heat or smoke.

(3)  If a material referred to in Sentence (2), consists of a number of discrete layers and testing reveals that the surface layer or layers protects the underlying layers such that the complete combustion of the underlying layers does not occur, the test shall be repeated by removing the outer layers sequentially until all layers have been exposed during testing, or complete combustion has occurred.

(4)  The acceptance criteria for a material tested in accordance with Sentence (3) shall be based on the cumulative emissions from all layers, which must not exceed the criteria stated in Clauses (2)(a) and (2)(b).

3.1.5.2.  Minor Combustible Components

(1)  The following minor combustible components are permitted in a building required to be of noncombustible construction:

(a)	paint,

(b)	mastics and caulking materials applied to provide flexible seals between the major components of exterior wall construction,

(c)	fire stop materials conforming to Sentence 3.1.9.1.(1) and Article 3.1.11.7.,

(d)	tubing for pneumatic controls provided it has an outside diameter not more than 10 mm,

(e)	adhesives, vapour barriers and sheathing papers,

(f)	electrical outlet and junction boxes,

(g)	wood blocking within wall assemblies intended for the attachment of handrails, fixtures, and similar items mounted on the surface of the wall, and

(h)	similar minor components.

3.1.5.3.  Combustible Roofing Materials

(1)  Combustible roof covering that has an A, B, or C classification determined in conformance with Subsection 3.1.15. is permitted on a building required to be of noncombustible construction.

(2)  Combustible roof sheathing and roof sheathing supports installed above a concrete deck are permitted on a building required to be of noncombustible construction provided,

(a)	the concrete deck is not less than 50 mm thick,

(b)	the height of the roof space above the deck is not more than 1 000 mm,

(c)	the roof space is divided into compartments by fire stops in conformance with Article 3.1.11.5.,

(d)	openings through the concrete deck other than for noncombustible roof drains and plumbing piping are protected by masonry or concrete shafts,

(i)	constructed as fire separations having a fire-resistance rating not less than 1 h, and

(ii)	extending from the concrete deck to not less than 150 mm above the adjacent roof sheathing,

(e)	the perimeter of the roof is protected by a noncombustible parapet extending from the concrete deck to not less than 150 mm above the adjacent sheathing, and

(f)	except as permitted by Clause (d), the roof space does not contain any building services.

(3)  Combustible cant strips, roof curbs, nailing strips and similar components used in the installation of roofing are permitted on a building required to be of noncombustible construction.

(4)  Wood nailer facings to parapets, not more than 600 mm high, are permitted on a building required to be of noncombustible construction, if the facings and any roof membranes covering the facings are protected by sheet metal.

3.1.5.4.  Combustible Glazing and Skylights

(1)  Combustible skylight assemblies are permitted in a building required to be of noncombustible construction if the assemblies have a flame-spread rating not more than,

(a)	150 provided the assemblies,

(i)	have an individual area not more than 9 m2,

(ii)	have an aggregate horizontal projected area of the openings through the ceiling not more than 25% of the area of the ceiling of the room or space in which they are located, and

(iii)	are spaced not less than 2 500 mm from adjacent assemblies and 1 200 mm from required fire separations, or

(b)	75 provided the assemblies,

(i)	have an individual area not more than 27 m2,

(ii)	have an aggregate horizontal projected area of the openings through the ceiling not more than 33% of the area of the ceiling of the room or space in which they are located, and

(iii)	are spaced not less than 1 200 mm from adjacent assemblies and from required fire separations.

(2)  Combustible vertical glazing installed no higher than the second storey is permitted in a building required to be of noncombustible construction.

(3)  Except as permitted by Sentence (4), the combustible vertical glazing permitted by Sentence (2) shall have a flame-spread rating not more than 75.

(4)  The flame-spread rating of combustible glazing in Sentence (2) is permitted to be not more than 150 if the aggregate area of glazing is not more than 25% of the wall area of the storey in which it is located, and

(a)	the glazing is installed in a building not more than 1 storey in building height,

(b)	the glazing in the first storey is separated from the glazing in the second storey in accordance with the requirements of Article 3.2.3.17. for opening protection, or

(c)	sprinklers are installed in,

(i)	any storey with combustible glazing, and

(ii)	the storey immediately above the storey with combustible glazing.

(5)  Combustible window sashes and frames are permitted in a building required to be of noncombustible construction provided,

(a)	each window in an exterior wall face is an individual unit separated by noncombustible wall construction from every other opening in the wall,

(b)	windows in exterior walls in contiguous storeys are separated by not less than 1 000 mm of noncombustible construction, and

(c)	the aggregate area of openings in an exterior wall face of a fire compartment is not more than 40% of the area of the wall face.

3.1.5.5.  Combustible Components for Exterior Walls

(1)  Except for an exposing building face required to conform to Sentence 3.2.3.7.(1) or Sentence 3.2.3.7.(4), an exterior non-loadbearing wall assembly that includes combustible components is permitted to be used in a building required to be of noncombustible construction provided,

(a)	the building is,

(i)	not more than 3 storeys in building height, or

(ii)	not more than 6 storeys in building height if sprinklered,

(b)	the interior surfaces of the wall assembly are protected by a thermal barrier conforming to Sentence 3.1.5.11.(3), and

(c)	the wall assembly satisfies the criteria of Sentences (2) and (3) when subjected to testing in conformance with CAN/ULC-S134, “Fire Test of Exterior Wall Assemblies”.

(2)  Flaming on or in the wall assembly shall not spread more than 5 m above the opening during the test procedure referenced in Sentence (1).

(3)  The heat flux during the flame exposure on a wall assembly shall be not more than 35 kW/m2 measured 3.5 m above the opening during the test procedure referenced in Sentence (1).

(4)  A wall assembly permitted by Sentence (1) that includes combustible cladding of fire-retardant treated wood shall be tested for fire exposure after the cladding has been subjected to an accelerated weathering test as specified in ASTM D2898, “Accelerated Weathering on Fire-Retardant-Treated Wood for Fire Testing”.

(5)  The requirements in this Article do not apply where foamed plastic insulation is used in an exterior wall assembly of a building and the insulation is protected in conformance with Sentences 3.2.3.8.(1) and (2).

3.1.5.6.  Nailing Elements

(1)  Wood nailing elements attached directly to or set into a continuous noncombustible backing for the attachment of interior finishes, are permitted in a building required to be of noncombustible construction provided the concealed space created by the wood elements is not more than 50 mm thick.

3.1.5.7.  Combustible Millwork

(1)  Combustible millwork including interior trim, doors and door frames, show windows together with their frames, aprons and backing, handrails, shelves, cabinets and counters is permitted in a building required to be of noncombustible construction.

3.1.5.8.  Combustible Flooring Elements

(1)  Combustible stage flooring supported on noncombustible structural members is permitted in a building required to be of noncombustible construction.

(2)  Wood members more than 50 mm but not more than 375 mm high applied directly to or set into a noncombustible floor slab are permitted for the construction of a raised platform in a building required to be of noncombustible construction provided the concealed spaces are fire stopped in conformance with Sentence 3.1.11.3.(2).

(3)  The floor system for the raised platform referred to in Sentence (2) is permitted to include combustible subfloor and combustible finished flooring.

(4)  Combustible finished flooring is permitted in a building required to be of noncombustible construction.

3.1.5.9.  Combustible Stairs in Dwelling Units

(1)  Combustible stairs are permitted in a dwelling unit in a building required to be of noncombustible construction.

3.1.5.10.  Combustible Interior Finish

(1)  Combustible interior finish, including paint, wallpaper, and other interior finishes not more than 1 mm thick, is permitted in a building required to be of noncombustible construction.

(2)  Combustible interior wall finishes, other than foamed plastics, are permitted in a building required to be of noncombustible construction provided they,

(a)	are not more than 25 mm thick, and

(b)	have a flame-spread rating not more than 150 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction.

(3)  Combustible interior ceiling finishes, other than foamed plastics, are permitted in a building required to be of noncombustible construction provided they,

(a)	are not more than 25 mm thick, except for exposed fire-retardant treated wood battens, and

(b)	have a flame-spread rating not more than 25 on any exposed surface, or on any surface that would be exposed by cutting through the material in any direction, or are of fire-retardant treated wood, except that not more than 10% of the ceiling area within each fire compartment is permitted to have a flame-spread rating not more than 150.

3.1.5.11.  Gypsum Board

(1)  Gypsum board with a tightly adhering paper covering not more than 1 mm thick is permitted in a building required to be of noncombustible construction provided the flame-spread rating of the surface is not more than 25.

3.1.5.12.  Combustible Insulation and its Protection

(1)  Combustible insulation, other than foamed plastics, is permitted in a building required to be of noncombustible construction provided that it has a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, where the insulation is not protected as described in Sentences (3) and (4).

(2)  Foamed plastic insulation having a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of,

(a)	not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation,

(b)	lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

(c)	masonry,

(d)	concrete, or

(e)	any thermal barrier that meets the requirements of classification B when tested in conformance with CAN4-S124-M, “Test for the Evaluation of Protective Coverings for Foamed Plastic”.

(3)  Combustible insulation having a flame-spread rating more than 25 but not more than 500 on an exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier as described in Sentence (2), except that in a building that is not sprinklered and is more than 18 m high, measured between grade and the floor level of the top storey, or in a building that is not sprinklered and is regulated by the provisions of Subsection 3.2.6., the insulation shall be protected by a thermal barrier consisting of,

(a)	gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled,

(b)	lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

(c)	masonry or concrete not less than 25 mm thick, or

(d)	any thermal barrier that, when tested in conformance with CAN/ULC-S101-M, “Fire Endurance Tests of Building Construction and Materials”, will not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 10 min.

(4)  Combustible insulation having a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier as described in Sentence (2), except that in a building that is not sprinklered and is more than 18 m high, measured between grade and the floor level of the top storey, or in a building that is not sprinklered and is regulated by the provisions of Subsection 3.2.6., the insulation shall be protected by a thermal barrier consisting of,

(a)	Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to,

(i)	CAN/CSA-A82.27-M, “Gypsum Board”,

(ii)	ASTM C36 / C36M, “Gypsum Wallboard”,

(iii)	ASTM C442 / C442M, “Gypsum Backing Board, Gypsum Coreboard, and Gypsum Shaftliner Board”,

(iv)	ASTM C588 / C588M, “Gypsum Base for Veneer Plasters”,

(v)	ASTM C630 / C630M, “Water-Resistant Gypsum Backing Board”,

(vi)	ASTM C931 / C931M, “Exterior Gypsum Soffit Board”, or

(vii)	ASTM C960 / C960M, “Predecorated Gypsum Board”,

(b)	non-loadbearing masonry or concrete not less than 50 mm thick,

(c)	loadbearing masonry or concrete not less than 75 mm thick, or

(d)	any thermal barrier that, when tested in conformance with CAN/ULC-S101-M, “Fire Endurance Tests of Building Construction and Materials”,

(i)	will not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 20 min, and

(ii)	will remain in place for not less than 40 min.

(5)  Combustible insulation, including foamed plastics, installed above roof decks, outside of foundation walls below ground level and beneath concrete slabs-on-ground is permitted to be used in a building required to be of noncombustible construction.

(6)  Thermosetting foamed plastic insulation having a flame-spread rating not more than 500 that forms part of a factory-assembled exterior wall panel that does not incorporate an air space is permitted to be used in a building required to be of noncombustible construction provided,

(a)	the foamed plastic is protected on both sides by sheet steel not less than 0.38 mm thick that will remain in place for not less than 10 min when the wall panel is tested in conformance with CAN/ULC-S101-M, “Fire Endurance Tests of Building Construction and Materials”,

(b)	the flame-spread rating of the wall panel, determined by subjecting a sample including an assembled joint to the appropriate test described in Subsection 3.1.12., is not more than the flame-spread rating permitted for the room or space that it bounds,

(c)	the building does not contain a Group B or Group C major occupancy, and

(d)	the building is not more than 18 m high, measured between grade and the floor level of the top storey.

(7)  A factory-assembled non-loadbearing interior or exterior wall or ceiling panel containing foamed plastic insulation having a flame-spread rating of not more than 500 is permitted to be used in a building required to be of noncombustible construction provided,

(a)	the building is sprinklered,

(b)	the building is not more than 18 m high, measured between grade and the floor level of the uppermost storey,

(c)	the building does not contain a Group A, Group B, or Group C major occupancy,

(d)	the panel does not contain an air space,

(e)	the panel, when tested in conformance with ULC/ORD-C376, “Fire Growth of Foamed Plastic Insulated Building Panels in a Full-Scale Room Configuration”, meets the criteria defined in the document, and

(f)	the flame-spread rating of a panel, determined by subjecting a sample, including an assembled joint typical of field installation, to the appropriate test described in Subsection 3.1.12., is not more than the flame-spread rating permitted for the room or space that it bounds.

3.1.5.13.  Combustible Elements in Partitions

(1)  Except as permitted by Sentence (2), solid lumber partitions not less than 38 mm thick and wood framing in partitions located in a fire compartment not more than 600 m2 in area are permitted to be used in a building required to be of noncombustible construction in a floor area that is not sprinklered provided the partitions,

(a)	are not required fire separations, and

(b)	are not located in a care or detention occupancy.

(2)  Partitions installed in a building of noncombustible construction are permitted to contain wood framing provided,

(a)	the building is not more than 3 storeys in building height,

(b)	the partitions are not located in a care or detention occupancy, and

(c)	the partitions are not installed as enclosures for exits or vertical service spaces.

(3)  Solid lumber partitions not less than 38 mm thick and partitions that contain wood framing are permitted to be used in a building required to be of noncombustible construction provided,

(a)	the floor area containing the partitions is sprinklered, and

(b)	the partitions are not,

(i)	located in a care or detention occupancy,

(ii)	installed as enclosures for exits or vertical service spaces, or

(iii)	used to satisfy the requirements of Clause 3.2.8.1.(1)(a).

3.1.5.14.  Storage Lockers in Residential Buildings

(1)  Storage lockers in storage rooms are permitted to be constructed of wood in a building of residential occupancy required to be of noncombustible construction.

3.1.5.15.  Combustible Ducts

(1)  Except as required by Sentence 3.6.4.3.(1), combustible ducts, including plenums and duct connectors, are permitted to be used in a building required to be of noncombustible construction provided these ducts and duct connectors are used only in horizontal runs.

(2)  Combustible duct linings, duct coverings, duct insulation, vibration isolation connectors, duct tape, pipe insulation and pipe coverings are permitted to be used in a building required to be of noncombustible construction provided they conform to the appropriate requirements of Part 6.

(3)  In a building required to be of noncombustible construction, combustible ducts need not comply with the requirements of Part 6 provided the ducts are,

(a)	part of a duct system conveying only ventilation air, and

(b)	contained entirely within a dwelling unit.

3.1.5.16.  Combustible Piping Materials

(1)  Except as permitted by Clause 3.1.5.2.(1)(d) , Sentences (2) and (3), and Article 3.1.5.22., combustible piping and tubing and associated adhesives are permitted to be used in a building required to be of noncombustible construction provided that, except when concealed in a wall or concrete floor slab, they,

(a)	have a flame-spread rating not more than 25, and

(b)	if used in a building described in Subsection 3.2.6., have a smoke developed classification not more than 50.

(2)  Combustible sprinkler piping is permitted to be used within a sprinklered floor area in a building required to be of noncombustible construction.

(3)  Polypropylene pipes and fittings are permitted to be used for drain, waste and vent piping for the conveyance of highly corrosive materials and for piping used to distribute distilled or dialyzed water in laboratory and hospital facilities in a building required to be of noncombustible construction, provided,

(a)	the building is sprinklered,

(b)	the piping is not located in a vertical shaft, and

(c)	piping that penetrates a fire separation is sealed at the penetration by a fire stop system that, when subjected to the fire test method in CAN4-S115-M, “Fire Tests of Firestop Systems”, has an FT rating not less than the fire-resistance rating of the fire separation.

3.1.5.17.  Combustible Plumbing Fixtures

(1)  Combustible plumbing fixtures are permitted in a building required to be of noncombustible construction if they are constructed of material having a flame-spread rating and smoke developed classification permitted in Subsection 3.1.13.

3.1.5.18.  Wires and Cables

(1)  Except as permitted by Articles 3.1.5.19. and 3.1.5.21., optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes are permitted in a building required to be of noncombustible construction, provided,

(a)	the wires and cables exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cabletrough in Clause 4.11.4. of CAN/CSA-C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating),

(b)	the wires and cables are located in,

(i)	totally enclosed noncombustible raceways,

(ii)	concealed spaces in walls,

(iii)	concrete slabs,

(iv)	a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or

(v)	totally enclosed nonmetallic raceways conforming to Article 3.1.5.20., or

(c)	the wires and cables are communication cables used at the service entry to a building and are not more than 3 m long.

(2)  The requirement in Clause (1)(a) is considered to be met where the wires and cables exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating).

3.1.5.19.  Combustible Travelling Cables for Elevators

(1)  Combustible travelling cables are permitted on elevating devices in a building required to be of noncombustible construction.

3.1.5.20.  Nonmetallic Raceways

(1)  Subject to limits on size for penetrations of fire separations as required by Sentence 3.1.9.3.(2), within a fire compartment of a building required to be of noncombustible construction, totally enclosed nonmetallic raceways not more than 175 mm in outside diameter, or an equivalent rectangular area, are permitted to be used to enclose optical fibre cables and electrical wires and cables, provided the raceways exhibit a vertical char not more than 1.5 m when tested in conformance with the Test for Flame Propagation (Riser) in Section 3.4 of the ULC/ORD-C2024, “Fire Tests for Optical Fibre Cable Raceways” (FT-4 rating).

3.1.5.21.  Wires in Computer Room Floors

(1)  Optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes, located in the space below a raised floor in a computer room, are permitted in a building required to be of noncombustible construction provided they do not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test in Clause 4.11.1. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT1 Rating).

(2)  The requirement in Sentence (1) is considered to be met where the wires and cables

(a)	exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test — Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating), or

(b)	exhibit a flame-spread of not more than 1.5 m, a smoke density of not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating).

3.1.5.22.  Combustible Components in Public Pools and Public Spas

(1)  Combustible fittings and components in a public pool or public spa, including main drains, piping, skimmers, return inlets, steps, ladder rungs and liners, are permitted in a building required to be of noncombustible construction.

3.1.5.23.  Marquees Having Combustible Elements

(1)  Except as permitted in Sentence (2), exterior marquees, not greater than 7.5 m from ground level to the top of the marquee, having combustible elements other than fabrics or films conforming to Sentence 3.1.16. 1.(1), are permitted on a building required to be of noncombustible construction, provided every opening in the exposed wall of the building above the marquee is protected with wired glass in accordance with Supplementary Standard SB-2 where these openings are within,

(a)	4.5 m horizontally of the marquee, and

(b)	9 m vertically above the marquee.

(2)  The protection required by Sentence (1) is permitted to be waived if the building is sprinklered.

3.1.5.24.  Combustible Mezzanines

(1)  In a building required to be of noncombustible construction, a mezzanine located within a live/work unit is permitted to be of combustible construction provided the area of the mezzanine is not more than 25% of the floor area of the live/work unit or 20 m2, whichever is less, and has no obstructions more than 1 070 mm above the floor.

3.1.5.25.  Wood Decorative Cladding

(1)  Wood decorative cladding is permitted to be used on exterior marquee fascias, of a storey having direct access to a street or access route, of a building required to be of noncombustible construction provided the cladding is fire-retardant treated wood that, before testing to CAN/ULC-S102-M, “Test for Surface Burning Characteristics of Building Materials and Assemblies,” has been conditioned in conformance with ASTM D 2898, “Accelerated Weathering of Fire-Retardant Treated Wood for Fire Testing”.

3.1.5.26.  Combustible Solar Collector Systems

(1)  A combustible solar collector system is permitted to be installed above the roof of a building required to be of non-combustible construction.

3.1.6.  Reserved

3.1.7.  Fire-Resistance Ratings

3.1.7.1.  Determination of Ratings

(1)  Except as permitted by Sentence (2) and Article 3.1.7.2., the rating of a material, assembly of materials or a structural member that is required to have a fire-resistance rating, shall be determined on the basis of the results of tests conducted in conformance with CAN/ULC-S101-M, “Fire Endurance Tests of Building Construction and Materials”.

(2)  A material, assembly of materials or a structural member is permitted to be assigned a fire-resistance rating on the basis of Supplementary Standard SB-2.

3.1.7.2.  Exception for Exterior Walls

(1)  The limit on the rise of temperature on the unexposed surface of an assembly as required by the tests referred to in Sentence 3.1.7.1.(1) shall not apply to an exterior wall that has a limiting distance of 1.2 m or more, provided correction is made for radiation from the unexposed surface in accordance with Sentence 3.2.3.1.(6).

3.1.7.3.  Exposure Conditions for Rating

(1)  Floor, roof and ceiling assemblies shall be rated for exposure to fire on the underside.

(2)  Firewalls and interior vertical fire separations shall be rated for exposure to fire on each side.

(3)  Exterior walls shall be rated for exposure to fire from inside the building.

3.1.7.4.  Minimum Fire-Resistance Rating

(1)  The use of materials or assemblies having a greater fire-resistance rating than required shall impose no obligation to exceed in whole or in part the minimum fire-resistance ratings required by this Part.

3.1.7.5.  Rating of Supporting Construction

(1)  Except as permitted by Sentence (2) and by Articles 3.2.2.20. to 3.2.2.83. for mixed types of construction, all loadbearing walls, columns and arches in the storey immediately below a floor or roof assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than that required for the supported floor or roof assembly.

(2)  Loadbearing walls, columns and arches supporting a service room or service space need not conform to Sentence (1).

(3)  If an assembly is required to be of noncombustible construction and have a fire-resistance rating, it shall be supported by noncombustible construction.

3.1.8.  Fire Separations and Closures

3.1.8.1.  General Requirements

(1)  Any wall, partition or floor assembly required to be a fire separation shall,

(a)	except as permitted by Sentence (2), be constructed as a continuous element, and

(b)	as required in this Part, have a fire-resistance rating as specified.

(2)  Openings in a fire separation shall be protected with closures, shafts or other means in conformance with Articles 3.1.8.4. to 3.1.8.18. and Subsections 3.1.9. and 3.2.8.

3.1.8.2.  Combustible Construction Support

(1)  Combustible construction that abuts on or is supported by a noncombustible fire separation shall be constructed so that its collapse under fire conditions will not cause the collapse of the fire separation.

3.1.8.3.  Continuity of Fire Separations

(1)  Except as permitted by Sentence 3.6.4.2.(2), a horizontal service space or other concealed space located above a required vertical fire separation, including the walls of a vertical shaft, shall be divided at the fire separation by an equivalent fire separation within the service space.

(2)  The fire separation required by Sentence (1) shall terminate so that smoke-tight joints are provided where it abuts on or intersects,

(a)	a floor,

(b)	a roof slab, or

(c)	a roof deck.

(3)  Except as required by Subsection 3.6.3. for a shaft penetrating a roof assembly, a shaft, including an exit enclosure, that penetrates a fire separation, shall,

(a)	extend through any horizontal service space or any other concealed space, and

(b)	terminate so that smoke-tight joints are provided where the shaft abuts on or intersects,

(i)	a floor,

(ii)	a roof slab, or

(iii)	a roof deck.

(4)  The continuity of a fire separation shall be maintained where it abuts another fire separation, a floor, a ceiling, or an exterior wall assembly.

3.1.8.4.  Determination of Ratings

(1)  Except as permitted by Sentences (2) and 3.1.8.14.(1), the fire-protection rating for a closure shall be determined on the basis of the results of tests conducted in conformance with the appropriate provisions in,

(a)	CAN4-S104-M, “Fire Tests of Door Assemblies”,

(b)	CAN4-S106-M, “ Fire Tests of Window and Glass Block Assemblies”, or

(c)	CAN/ULC-S112-M, “Fire Test of Fire-Damper Assemblies”.

(2)  Except as permitted by Sentence 3.1.8.10.(1), the fire-protection rating of a closure shall conform to Table 3.1.8.4. for the required fire-resistance rating of the fire separation.

Table 3.1.8.4.
Fire-Protection Rating of Closure

Forming Part of Sentence 3.1.8.4.(2)

| Column 1 | Column 2 |
| --- | --- |
| Fire-Resistance Rating of Fire Separation | Required Fire-Protection Rating of Closure |
| 30 min | 20 min |
| 45 min | 45 min |
| 1 h | 45 min |
| 1.5 h | 1 h |
| 2 h | 1.5 h |
| 3 h | 2 h |
| 4 h | 3 h |

3.1.8.5.  Installation of Closures

(1)  Except where fire dampers, window assemblies and glass block are used as closures, closures of the same fire-protection rating installed on opposite sides of the same opening are deemed to have a fire-protection rating equal to the sum of the fire-protection ratings of the closures.

(2)  Except as otherwise specified in this Part, every door, window assembly or glass block used as a closure in a required fire separation,

(a)	shall be installed in conformance with NFPA 80, “Standard for Fire Doors and Fire Windows”, and

(b)	where required to have a fire-protection rating, shall have labels or classification marks to identify the testing laboratory.

(3)  If a door is installed so that it could damage the integrity of a fire separation if its swing is unrestricted, door stops shall be installed to prevent the damage.

3.1.8.6.  Maximum Openings

(1)  The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 11 m2, with no dimension more than 3.7 m, if a fire compartment on either side of the fire separation is not sprinklered.

(2)  The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 22 m2, with no dimension more than 6 m, provided the fire compartments on both sides of the fire separation are sprinklered.

3.1.8.7.  Fire Dampers

(1)  Except as permitted by Article 3.1.8.8., a duct that penetrates an assembly required to be a fire separation shall be equipped with a fire damper.

3.1.8.8.  Fire Dampers Waived

(1)  Fire dampers need not be provided in noncombustible branch ducts that have a melting point above 760°C and that penetrate a required fire separation provided the ducts,

(a)	serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1 200 mm above the floor and have a cross-sectional area not more than 0.013 m2, or

(b)	are connected to exhaust duct risers that are under negative pressure and in which the air flow is upward as required by Article 3.6.3.4. and are carried up inside the riser not less than 500 mm.

(2)  A continuous noncombustible duct penetrating a vertical fire separation not required to have a fire-resistance rating need not be equipped with a fire damper at the fire separation.

(3)  A noncombustible duct that penetrates a horizontal fire separation not required to have a fire-resistance rating need not be equipped with a fire damper at the fire separation.

(4)  A noncombustible duct that penetrates a fire separation that separates a vertical service space from the remainder of the building need not be equipped with a fire damper at the fire separation provided,

(a)	the duct has a melting point above 760°C, and

(b)	each individual duct exhausts directly to the outside at the top of the vertical service space.

(5)  A continuous noncombustible duct having a melting point above 760°C that penetrates a vertical fire separation as required by Sentence 3.3.1.1.(1) between suites of other than residential or care or detention occupancy need not be equipped with a fire damper at the fire separation.

(6)  A duct that serves commercial cooking equipment and penetrates a required fire separation need not be equipped with a fire damper at the fire separation.

(7)  In elementary and secondary schools, a continuous noncombustible duct having a melting point above 760°C that pierces a fire separation having a fire-resistance rating of 30 min need not be equipped with a fire damper at the fire separation.

(8)  In a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants require assistance in evacuation in case of an emergency and which is equipped with a fire-alarm system, a duct need not be provided with a fire-damper at a fire separation provided duct-type smoke detectors have been installed to control smoke circulation as described in Article 3.2.4.12.

3.1.8.9.  Installation of Fire Dampers

(1)  A fire damper shall be arranged to close automatically upon the operation of a fusible link conforming to ULC-S505, “Fusible Links for Fire Protection Service”, or other heat-actuated or smoke-actuated device.

(2)  A heat-actuated device referred to in Sentence (1) shall,

(a)	be located where it is readily affected by an abnormal rise of temperature in the duct, and

(b)	have a temperature rating approximately 30°C above the maximum temperature that would exist in the system either with the system in operation or shut down.

(3)  A fire damper shall be installed in the plane of the fire separation so as to stay in place should the duct be dislodged during a fire.

(4)  A fire damper tested in the vertical or horizontal position shall be installed in the manner in which it was tested.

(5)  A tightly fitted access door shall be installed for each fire damper to provide access for the inspection of the damper and the resetting of the release device.

3.1.8.10.  Twenty-Minute Closures

(1)  A door assembly having a fire-protection rating not less than 20 min is permitted to be used as a closure in,

(a)	a fire separation not required to have a fire-resistance rating more than 1 h, located between,

(i)	a public corridor and a suite,

(ii)	a corridor and adjacent sleeping rooms, or

(iii)	a corridor and adjacent classrooms, offices and libraries in Group A, Division 2 major occupancies, or

(b)	a fire separation not required to have a fire-resistance rating more than 45 min, located in a building not more than 3 storeys in building height.

(2)  The requirements for noncombustible sills and combustible floor coverings in NFPA 80, “Fire Doors and Fire Windows”, do not apply to a door described in Sentence (1).

(3)  A door described in Sentence (1) shall have a clearance not more than 6 mm at the bottom and not more than 3 mm at the sides and top.

(4)  In elementary and secondary schools, a door assembly conforming to Articles 9.10.13.2. and 9.10.13.3. is permitted to be used as a closure in a fire separation having a fire-resistance rating of 30 min.

3.1.8.11.  Self-Closing Devices

(1)  Except as provided in Sentences (2) to (5) and 3.3.3.2.(5), every door in a fire separation shall be equipped with a self-closing device designed to return the door to the closed position after each use.

(2)  Self-closing devices need not be provided on doors to freight elevators and dumbwaiters.

(3)  In a building that is not more than 3 storeys in building height, a self-closing device is not required on a door that is located between a classroom and a corridor providing access to exit from the classroom, except that a self-closing device is required on a door between a hazardous classroom and the corridor in an elementary or secondary school.

(4)  In a building that is not more than 3 storeys in building height, a self-closing device is not required on a door between a public corridor and an adjacent room or suite of business and personal services occupancy if the door is not located in,

(a)	a dead-end portion of the corridor, or

(b)	a corridor that serves a hotel.

(5)  Within a fire compartment in a hospital or nursing home that complies with the requirements of Article 3.3.3.5., a self-closing device is not required on a door that is located between,

(a)	a patient’s or resident’s sleeping room and a corridor serving the patient’s or resident’s sleeping room, or

(b)	a patient’s or resident’s sleeping room and an adjacent room that serves the patient’s or resident’s sleeping room.

3.1.8.12.  Hold-Open Devices

(1)  A hold-open device is permitted on a door in a required fire separation, other than an exit door in a building more than 3 storeys in building height, and on a door for a vestibule required by Article 3.3.5.7., provided the device is designed to release the door in conformance with Sentences (2) to (7).

(2)  Except as required by Sentences (3), (5), (6) and (7), a hold-open device permitted by Sentence (1) shall be designed to release by a signal from,

(a)	an automatic sprinkler system,

(b)	a heat-actuated device,

(c)	fusible link, or

(d)	a smoke detector located as described in Appendix B of NFPA 80, “Fire Doors and Fire Windows”.

(3)  Except as required by Sentences (4), (5), (6) and (7), a hold-open device permitted by Sentence (1) shall be designed to release upon a signal from a smoke detector located as described in Appendix B of NFPA 80, “Fire Doors and Fire Windows”, if used on,

(a)	an exit door,

(b)	a door opening into a public corridor,

(c)	an egress door referred to in Sentence 3.4.2.4.(2),

(d)	a door serving,

(i)	an assembly occupancy,

(ii)	a care or detention occupancy, or

(iii)	a residential occupancy, or

(e)	a door required to function as part of a smoke control system.

(4)  Except as required by Sentence (5), (6) and (7), a hold-open device permitted by Sentence (1) shall be designed to release upon a signal from the building fire alarm system if a fire alarm system is provided, except that this requirement does not apply to,

(a)	a hold-open device on a door located between a corridor used by the public and an adjacent sleeping room in a hospital or nursing home, or

(b)	a hold-open device that is designed to release by a heat-actuated device or a fusible link in conformance with Sentence (2).

(5)  Sentences (2) and (3) do not apply in a hospital or nursing home to,

(a)	a door located between a corridor used by the public and an adjacent sleeping room, or

(b)	paired doors described in Sentence 3.3.3.3.(4).

(6)  A hold-open device on a door in Clause (5)(a) shall be designed to release the door upon a signal from,

(a)	a smoke detector as required by Sentence 3.2.4.11.(1) for sleeping rooms in Group B occupancies, and

(b)	the fire alarm system when an alert signal is initiated within the same fire compartment in Sentence 3.3.3.5.(2).

(7)  A hold-open device on a door in Clause (5)(b) shall be designed to release the door upon a signal from the fire alarm system when an alert signal is initiated within the same fire compartment in Sentence 3.3.3.5.(2).

(8)  A rolling steel fire door installed as a closure in a fire separation shall be equipped with a hold-open device designed to release the shutter as described in Sentence (2).

3.1.8.13.  Door Latches

(1)  Except as permitted by Sentence 3.3.3.2.(5) and Article 3.3.3.5., a swing-type door in a fire separation shall be equipped with a positive latching mechanism designed to hold the door in the closed position after each use.

3.1.8.14.  Wired Glass and Glass Block

(1)  Except as permitted by Articles 3.1.8.16. and 3.1.8.17. for the separation of exits, an opening in a fire separation having a fire-resistance rating not more than 1 h is permitted to be protected with fixed wired glass assemblies or glass blocks installed in conformance with NFPA 80, “Fire Doors and Fire Windows”.

(2)  Wired glass assemblies permitted by Sentence (1) and described in Supplementary Standard SB-2, are permitted to be used as closures in vertical fire separations without being tested in accordance with Sentence 3.1.8.4.(1).

(3)  Glass blocks permitted by Sentence (1) shall be installed in accordance with Subsection 4.3.2. and reinforced with steel reinforcement in each horizontal joint.

3.1.8.15.  Temperature Rise Limit for Doors

(1)  Except as permitted by Article 3.1.8.17., the maximum temperature rise on the opaque portion of the unexposed side of a door used as a closure in a fire separation in a location shown in Table 3.1.8.15., shall conform to the Table when tested in conformance with Sentence 3.1.8.4.(1).

3.1.8.16.  Area Limits for Wired Glass and Glass Block

(1)  Except as permitted by Article 3.1.8.17., the maximum area of wired glass in a door used in the locations shown in Table 3.1.8.15. shall conform to the Table.

(2)  Except as permitted by Article 3.1.8.17., the maximum area of glass block and wired glass panels not in a door, used in the locations shown in Table 3.1.8.15., shall conform to the Table.

Table 3.1.8.15.
Restrictions on Temperature Rise and Glazing for Closures

Forming Part Articles of 3.1.8.15. and 3.1.8.16.

| Column 1 | Column 2 | Column 3 | Column 4 | Column 5 |
| --- | --- | --- | --- | --- |
| Location | Minimum Required Fire-Protection Rating of Door | Maximum Temperature Rise on Opaque Portion of Unexposed Side of Door, °C | Maximum Area of Wired Glass in Door, m2 | Maximum Aggregate Area of Glass Block and Wired Glass Panels not in Door, m2 |
| Between a dead-end corridor and an adjacent occupancy where the corridor provides the only access to exit and is required to have a fire-resistance rating | Less than 45 min | No limit | No limit | No limit |
|  | 45 min | 250 after 30 min | 0.0645 | 0.0645 |
| Between an exit enclosure and the remainder of the floor area in buildings not more than 3 storeys in building height | All ratings | No limit | 0.8 | 0.8 |
| Between an exit enclosure and the remainder of the floor area (except as permitted above) | 45 min | 250 after 30 min | 0.0645 | 0.0645 |
|  | 1.5 h | 250 after 1 h | 0.0645 | 0.0645 |
|  | 2 h | 250 after 1 h | 0.0645 | 0.0645 |
| In a firewall | 1.5 h | 250 after 30 min | 0.0645 | 0 |
|  | 3 h | 250 after 1 h | 0 | 0 |

3.1.8.17.  Temperature Rise and Area Limits Waived

(1)  The temperature rise limits and glass area limits required by Articles 3.1.8.15. and 3.1.8.16. are waived for a closure between an exit enclosure and an enclosed vestibule or corridor provided,

(a)	the vestibule or corridor is separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min,

(b)	the fire separation required by Clause (a) contains no wired glass or glass block within 3 m of the closure into the exit enclosure, and

(c)	the vestibule or corridor contains no occupancy.

3.1.8.18.  Sprinkler Protected Glazed Wall Assembly

(1)  A sprinkler protected glazed wall assembly shall be constructed in accordance with the requirements of ULC/ORD C263.1, “Sprinkler-Protected Windows Systems”.

(2)  A sprinkler protected glazed wall assembly shall not be installed in,

(a)	fire separations requiring a fire resistance rating of more than 2 hours,

(b)	a firewall,

(c)	a high hazard industrial occupancy, or

(d)	any part of an exit serving,

(i)	a floor area subject to the requirements of Subsection 3.2.6.,

(ii)	a care and detention occupancy, or

(iii)	a residential occupancy.

(3)  Where a sprinkler protected glazed wall assembly is installed in an exit fire separation permitted in Sentence (2),

(a)	the building shall be sprinklered, and

(b)	the exits protected with the sprinkler protected glazed wall assemblies shall not comprise more than one half of the required number of exits from any floor area.

3.1.9.  Building Services in Fire Separations and Fire Rated Assemblies

3.1.9.1.  Fire Stopping of Service Penetrations

(1)  Except as required by Sentence (2), piping, tubing, ducts, chimneys, optical fibre cables, electrical wires and cables, totally enclosed noncombustible raceways, electrical outlet boxes and other similar building services that penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating, shall be,

(a)	sealed by a fire stop system that, when subjected to the fire test method in ULC-S115, “Fire Tests for Fire Stop Systems”, has an F rating not less than the fire-protection rating required for closures in the fire separation in conformance with Table 3.1.8.4., or

(b)	tightly fitted.

(2)  Piping, tubing, ducts, chimneys, optical fibre cables, electrical wires and cables, totally enclosed noncombustible raceways, electrical outlet boxes and other similar building services that penetrate a firewall or a horizontal fire separation that is required to have a fire-resistance rating in conformance with Article 3.2.1.2., shall be sealed at the penetration by a fire stop system that, when subjected to the fire test method in CAN4-S115-M, “Fire Tests of Firestop Systems”, has an FT rating not less than the fire-resistance rating for the fire separation.

3.1.9.2.  Combustibility of Service Penetrations

(1)  Except as permitted by Articles 3.1.9.3. and 3.1.9.4., pipes, ducts, electrical outlet boxes, totally enclosed raceways or other similar service equipment that penetrate an assembly required to have a fire-resistance rating shall be noncombustible unless the assembly has been tested incorporating that service equipment.

3.1.9.3.  Penetration by Wires, Cables and Outlet Boxes

(1)  Optical fibre cables and electrical wires and cables in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2.

(2)  Except as permitted by Sentence (3), totally enclosed nonmetallic raceways conforming to Article 3.1.5.20, optical fibre cables, and electrical wires and cables, single or grouped, with combustible insulation, jackets or sheathes that conform to the requirements of Clause 3.1.5.18.(1)(a) and that are not installed in totally enclosed noncombustible raceways are permitted to penetrate an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the overall diameter of the single or grouped wires or cables, or the raceways is not more than 25 mm.

(3)  Single conductor metal sheathed cables with combustible jacketing that are more than 25 mm (1 in) in overall diameter are permitted to penetrate a fire separation required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the cables are not grouped.

(4)  Combustible totally enclosed raceways that are embedded in a concrete floor slab are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the concrete cover between the raceway and the bottom of the slab is not less than 50 mm.

(5)  Combustible outlet boxes are permitted in an assembly required to have a fire-resistance rating without being incorporated in the assembly at the time of testing as required by Article 3.1.9.2., provided the opening through the membrane into the box is not more than 0.016 m2.

(6)  Outlet boxes that penetrate opposite sides of a wall assembly shall be offset where necessary to maintain the integrity of the fire separation.

3.1.9.4.  Combustible Piping Penetrations

(1)  Combustible sprinkler piping is permitted to penetrate a fire separation provided the fire compartments on each side of the fire separation are sprinklered.

(2)  Reserved

(3)  Except as permitted by Sentences (4) to (8), combustible piping shall not be used if any part of that system penetrates,

(a)	a fire separation required to have a fire-resistance rating, or

(b)	a membrane that forms part of an assembly required to have a fire-resistance rating.

(4)  Combustible piping is permitted to penetrate a fire separation required to have a fire-resistance rating or a membrane that forms part of an assembly required to have a fire-resistance rating, provided,

(a)	the piping is sealed at the penetration by a fire stop system that has an F rating not less than the fire-resistance rating required for the fire separation when subjected to the fire test method in CAN4-S115-M, “Fire Tests of Firestop Systems”, with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side, and

(b)	the piping is not located in a vertical shaft.

(5)  Combustible drain piping is permitted to penetrate a horizontal fire separation provided it leads directly from a noncombustible water closet through a concrete floor slab.

(6)  Combustible piping is permitted on one side of a vertical fire separation provided it is not located in a vertical shaft.

(7)  Combustible piping is permitted to penetrate a vertical or horizontal fire separation provided the fire compartments on each side of the fire separation are sprinklered.

(8)  Combustible piping not more 25 mm in diameter containing chlorine gas is permitted to penetrate a fire separation between a chlorine gas service room built in conjunction with a public pool or public spa, and the remainder of the building.

3.1.9.5.  Openings through a Membrane Ceiling

(1)  A membrane ceiling forming part of an assembly assigned a fire-resistance rating on the basis of Supplementary Standard SB-2 is permitted to be penetrated by openings leading into ducts within the ceiling space provided,

(a)	the ducts are sheet steel, and

(b)	the amount of openings and their protection conform to the requirements of Supplementary Standard SB-2.

(2)  Fire stop flaps in ceiling membranes required in Sentence (1) shall conform to CAN4-S112.2-M, “Fire Test of Ceiling Firestop Flap Assemblies”.

3.1.9.6.  Plenums

(1)  A ceiling assembly used as a plenum shall conform to Article 3.6.4.3.

3.1.10.  Firewalls

3.1.10.1.  Prevention of Firewall Collapse

(1)  Except as permitted by Sentence (2), the connections and supports for structural framing members that are connected to or supported on a firewall and have a fire-resistance rating less than that required for the firewall, shall be designed so that the failure of the framing systems during a fire will not affect the integrity of the firewall during the fire.

(2)  Sentence (1) does not apply to a firewall consisting of two separate wall assemblies each tied to its respective building frame but not to each other, provided each wall assembly is,

(a)	a fire separation having one half of the fire-resistance rating required for the firewall by Sentences 3.1.10.2.(1) and (2), and

(b)	designed so that the collapse of one wall assembly will not cause collapse of the other.

(3)  A firewall is permitted to be supported on the structural frame of a building of noncombustible construction provided the supporting frame has a fire-resistance rating not less than that required for the firewall.

(4)  Piping, ducts and totally enclosed noncombustible raceways shall be installed so that their collapse will not cause collapse of the firewall.

3.1.10.2.  Rating of Firewalls

(1)  A firewall that separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h, except that where the upper portion of a firewall separates floor areas containing other than Group E or Group F, Division 1 or 2 major occupancies, the fire-resistance rating of the upper portion of the firewall is permitted to be not less than 2 h.

(2)  A firewall that separates a building or buildings with floor areas containing major occupancies other than Group E or Group F, Division 1 or 2 shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 2 h.

(3)  Except as permitted by Sentence (4), the required fire-resistance rating of a firewall, except for closures, shall be provided by masonry or concrete.

(4)  A firewall permitted to have a fire-resistance rating not more than 2 h need not be constructed of masonry or concrete provided,

(a)	the assembly providing the fire-resistance rating is protected against damage that would compromise the integrity of the assembly,

(b)	the design conforms to Article 4.1.5.18.,

(c)	the level of performance of the firewall is not less than of masonry or concrete in the areas of

(i)	performance during fire conditions,

(ii)	mechanical damage during the normal use of the building, and

(iii)	resistance to damage from moisture,

(d)	the firewall separates buildings or buildings with floor areas that do not contain,

(i)	a Group B, Division 1 major occupancy, or

(ii)	a Group B, Division 2 major occupancy, and

(e)	the firewall does not separate buildings regulated by the provisions of Subsection 3.2.6.

3.1.10.3.  Continuity of Firewalls

(1)  A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated, except that a firewall located above a basement storage garage conforming to Article 3.2.1.2. is permitted to commence at the floor assembly immediately above the storage garage.

(2)  A firewall is permitted to terminate on the underside of a reinforced concrete roof slab provided,

(a)	the roof slab on both sides of the firewall has a fire-resistance rating not less than,

(i)	1 h if the firewall is required to have a fire-resistance rating not less than 2 h, or

(ii)	2 h if the firewall is required to have a fire-resistance rating not less than 4 h, and

(b)	there are no concealed spaces within the roof slab in that portion immediately above the firewall.

3.1.10.4.  Parapets

(1)  Except as permitted by Sentences (2) and 3.1.10.3.(2), a firewall shall extend above the roof surface to form a parapet not less than,

(a)	150 mm high for a firewall required to have a fire-resistance rating not less than 2 h, and

(b)	900 mm high for a firewall required to have a fire-resistance rating not less than 4 h.

(2)  A firewall that separates 2 buildings with roofs at different elevations need not extend above the upper roof surface to form a parapet, provided the difference in elevation between the roofs is more than 3 m.

3.1.10.5.  Maximum Openings

(1)  Openings in a firewall shall conform to the size limits described in Article 3.1.8.6. and the aggregate width of openings shall be not more than 25% of the entire length of the firewall.

3.1.10.6.  Exposure Protection for Adjacent Walls

(1)  The requirements of Article 3.2.3.14. shall apply to the external walls of 2 buildings that meet at a firewall at an angle less than 135.

3.1.10.7.  Combustible Projections

(1)  Combustible material shall not extend across the end of a firewall but is permitted to extend across a roof above a firewall that is terminated in conformance with Sentence 3.1.10.3.(2).

(2)  If buildings are separated by a firewall, combustible projections on the exterior of one building, including balconies, platforms, canopies, eave projections and stairs, that extend outward beyond the end of the firewall, shall not be permitted within 2 400 mm of combustible projections and window or door openings of the adjacent building.

3.1.11.  Fire Stops in Concealed Spaces

3.1.11.1.  Separation of Concealed Spaces

(1)  Concealed spaces in interior wall, ceiling and crawl spaces shall be separated from concealed spaces in exterior walls and attic or roof spaces by fire stops conforming to Article 3.1.11.7.

3.1.11.2.  Fire Stopping in Wall Assemblies

(1)  Except as permitted by Sentence (2), fire stops conforming to Article 3.1.11.7. shall be provided to block off concealed spaces within a wall assembly,

(a)	at every floor level,

(b)	at every ceiling level where the ceiling forms part of an assembly required to have a fire-resistance rating, and

(c)	so that the maximum horizontal dimension is not more than 20 m and the maximum vertical dimension is not more than 3 m.

(2)  Fire stops conforming to Sentence (1) are not required provided,

(a)	the wall space is filled with insulation,

(b)	the exposed construction materials and any insulation within the wall space are noncombustible,

(c)	the exposed construction materials and any insulation within the wall space have a flame-spread rating not more than 25 on any exposed surface, or on any surface that would be exposed by cutting through the material in any direction, and fire stops are installed so that the vertical distance between them is not more than 10 m, or

(d)	the insulated wall assembly contains not more than one concealed air space, and the horizontal thickness of that air space is not more than 25 mm.

3.1.11.3.  Fire Stopping between Nailing and Supporting Elements

(1)  In a building required to be of noncombustible construction, a concealed space in which there is an exposed ceiling finish with a flame-spread rating more than 25, shall be provided with fire stops conforming to Article 3.1.11.7. between wood nailing elements, so that the maximum area of the concealed space is not more than 2 m2.

(2)  In a building required to be of noncombustible construction, fire stops conforming to Article 3.1.11.7. shall be provided in the concealed spaces created by the wood members permitted by Sentence 3.1.5.8.(2) so that the maximum area of a concealed space is not more than 10 m2.

3.1.11.4.  Fire Stopping between Vertical and Horizontal Spaces

(1)  Fire stops conforming to Article 3.1.11.7. shall be provided,

(a)	at all interconnections between concealed vertical and horizontal spaces in interior coved ceilings, drop ceilings and soffits in which the exposed construction materials within the space have a flame-spread rating more than 25, and

(b)	at the end of each run and at each floor level in concealed spaces between stair stringers in which the exposed construction materials within the space have a flame-spread rating more than 25.

3.1.11.5.  Fire Stopping of Horizontal Concealed Spaces

(1)  Except for a crawl space conforming to Sentence 3.1.11.6.(1), a horizontal concealed space within a floor assembly or roof assembly of combustible construction, in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than,

(a)	600 m2 in area with no dimension more than 60 m if the exposed construction materials within the space have a flame-spread rating not more than 25, and

(b)	300 m2 in area with no dimension more than 20 m if the exposed construction materials within the space have a flame-spread rating more than 25.

(2)  A concealed space in an exterior cornice, a mansard style roof, a balcony or a canopy in which exposed construction materials within the space have a flame-spread rating more than 25, shall be separated by construction conforming to Article 3.1.11.7.,

(a)	at locations where the concealed space extends across the ends of required vertical fire separations, and

(b)	so that the maximum dimension in the concealed space is not more than 20 m.

3.1.11.6.  Fire Stopping of Crawl Spaces

(1)  A crawl space that is not considered as a basement by Article 3.2.2.9. and in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than 600 m2 in area with no dimension more than 30 m.

3.1.11.7.  Fire Stop Materials

(1)  Except as permitted by Sentences (2) to (4) and (7) materials used to separate concealed spaces into compartments shall remain in place and prevent the passage of flames for not less than 15 min when subjected to the standard fire exposure in CAN/ULC-S101-M, “Fire Endurance Tests of Building Construction and Materials”.

(2)  Gypsum board not less than 12.7 mm thick and sheet steel not less than 0.38 mm thick need not be tested in conformance with Sentence (1) provided all joints have continuous support.

(3)  In a building required to be of noncombustible construction, wood nailing elements described in Article 3.1.5.6. need not be tested in conformance with Sentence (1).

(4)  In a building permitted to be of combustible construction, in a combustible roof system permitted by Sentence 3.1.5.3.(2), and in a raised platform permitted by Sentence 3.1.5.8.(2), materials used to separate concealed spaces into compartments are permitted to be,

(a)	solid lumber not less than 38 mm thick,

(b)	phenolic bonded plywood, waferboard, or strandboard not less than 12.5 mm thick with joints supported, or

(c)	two thicknesses of lumber, each not less than 19 mm thick with joints staggered, where the width or height of the concealed space requires more than one piece of lumber not less than 38 mm thick to block off the space.

(5)  Openings through materials referred to in Sentences (1) to (4) shall be protected to maintain the integrity of the construction.

(6)  Where materials referred to in Sentences (1) to (4) are penetrated by construction elements or by service equipment, fire stop materials shall be used to seal the penetration.

(7)  In a building permitted to be of combustible construction, semi-rigid fibre insulation board, produced from glass, rock or slag, is permitted to be used to block the vertical space in a double wythe wall assembly formed at the intersection of the floor assembly and the walls, provided the insulation board,

(a)	has a density not less than 45 kg/m3,

(b)	is securely fastened to one set of studs,

(c)	extends from below the bottom of the top plates in the lower storey to above the top of the bottom plate in the upper storey, and

(d)	completely fills the portion of the vertical space between the headers and between the wall plates.

3.1.12.  Flame-Spread Rating and Smoke Developed Classification

3.1.12.1.  Determination of Ratings

(1)  Except as required by Sentence (2) and as permitted by Sentence (3), the flame-spread rating and smoke developed classification of a material, assembly, or structural member shall be determined on the basis of no fewer than three tests conducted in conformance with CAN/ULC-S102-M, “Test for Surface Burning Characteristics of Building Materials and Assemblies”.

(2)  The flame-spread rating and smoke developed classification of a material or assembly shall be determined on the basis of no fewer than three tests conducted in conformance with CAN/ULC-S102.2, “Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies”, if the material or assembly,

(a)	is designed for use in a relatively horizontal position with only its top surface exposed to air,

(b)	cannot be tested in conformance with Sentence (1) without the use of supporting material that is not representative of the intended installation, or

(c)	is thermoplastic.

(3)  A material, assembly, or structural member is permitted to be assigned a flame-spread rating and smoke developed classification on the basis of Supplementary Standard SB-2.

3.1.13.  Interior Finish

3.1.13.1.  Interior Finish Description

(1)  Interior finish material shall include any material that forms part of the interior surface of a floor, wall, partition or ceiling, including,

(a)	interior cladding of plaster, wood or tile,

(b)	surfacing of fabric, paint, plastic, veneer or wallpaper,

(c)	doors, windows and trim,

(d)	lighting elements, such as light diffusers and lenses forming part of the finished surface of the ceiling, and

(e)	carpet material that overlies a floor that is not intended as the finished floor.

3.1.13.2.  Flame-Spread Rating

(1)  Except as otherwise required or permitted by this Subsection, the flame-spread rating of interior wall and ceiling finishes, including glazing and skylights, shall be not more than 150 and shall conform to Table 3.1.13.2.

(2)  Except as permitted by Sentence (3), doors, other than those in Group A, Division 1 occupancies, need not conform to Sentence (1) provided they have a flame-spread rating not more than 200.

(3)  Doors within a dwelling unit need not conform to Sentences (1) and (2).

(4)  Up to 10% of the total wall area and 10% of the total ceiling area of a wall or ceiling finish that is required by Sentence (1) to have a flame-spread rating less than 150 is permitted to have a flame-spread rating not more than 150, except that up to 25% of the total wall area of lobbies described in Sentence 3.4.4.2.(2) is permitted to have a flame-spread rating not more than 150.

(5)  Except in the case of Group A, Division 1 occupancies, combustible doors, skylights, glazing and light diffusers and lenses shall not be considered in the calculation of wall and ceiling areas described in Sentence (4).

Table 3.1.13.2.
Flame-Spread Ratings

Forming Part of Sentence 3.1.13.2.(1)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Occupancy, Location or Element | Maximum Flame-Spread Rating for Walls and Ceilings |  |
|  | Sprinklered | Not Sprinklered |
| Group A, Division 1 occupancies, including doors, skylights, glazing and light diffusers and lenses | 150 | 75 |
| Group B occupancies | 150 | 75 (2) |
| Exits(1) | 25 | 25 |
| Lobbies described in Sentence 3.4.4.2.(2) | 25 | 25 |
| Covered vehicular passageways, except for roof assemblies of heavy timber construction in such passageways | 25 | 25 |
| Vertical service spaces | 25 | 25 |

Notes to Table 3.1.13.2.:

(1) See Articles 3.1.13.8. and 3.1.13.10.

(2) Group B occupancies are required to be sprinklered. See Part 11 for renovations of existing non-sprinklered Group B occupancies.

3.1.13.3.  Bathrooms in Residential Suites

(1)  The flame-spread rating of interior wall and ceiling finishes for a bathroom in a suite of residential occupancy shall be not more than 200.

(2)  Plumbing fixtures shall have a flame-spread rating not more than 200.

3.1.13.4.  Light Diffusers and Lenses

(1)  The flame-spread rating of combustible light diffusers and lenses in all occupancies other than Group A, Division 1 is permitted to be more than the flame-spread rating limits required elsewhere in this Subsection, provided the light diffusers and lenses,

(a)	have a flame-spread rating not more than 250 and a smoke developed classification not more than 600 when tested in conformance with CAN/ULC-S102.2, “Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies”,

(b)	fall to the bottom of the test apparatus before igniting when tested in conformance with ULC-S102.3-M, “Fire Test of Light Diffusers and Lenses”,

(c)	are not prevented from falling from the ceiling by construction located beneath the elements, and

(d)	are not used in a corridor that is required to be separated from the remainder of the building by a fire separation or in an exit shaft unless individual diffusers or lenses are not more than 1 m2 in area and are not less than 1 200 mm apart.

3.1.13.5.  Skylights

(1)  Individual combustible skylights in a corridor that is required to be separated from the remainder of the building by a fire separation shall be not more than 1 m2 in area and not less than 1 200 mm apart.

3.1.13.6.  Corridors

(1)  Except as permitted by Sentences (2) and (3), the flame-spread rating shall be not more than 75 for the interior wall finish of,

(a)	a public corridor,

(b)	a corridor used by the public in,

(i)	an assembly occupancy, or

(ii)	a care or detention occupancy,

(c)	a corridor serving classrooms, or

(d)	a corridor serving sleeping rooms in a care or detention occupancy.

(2)  The flame-spread rating limit specified in Sentence (1) does not apply to corridors referred to in Sentence (1) provided the flame-spread rating is not more than,

(a)	25 on the upper half of the wall, and

(b)	150 on the lower half of the wall.

(3)  The flame-spread rating limits specified in Sentences (1) and (2) for corridors referred to in Sentence (1) does not apply to a corridor in which the flame-spread rating is not more than 150 provided the floor area is sprinklered.

(4)  The flame-spread rating limits specified in Sentences (1), (2) and (3) apply to occupancies in the corridor as well as to the corridor itself.

(5)  Except in a floor area that is sprinklered and as permitted in Sentence (6), the interior ceiling finish of corridors and occupancies referred to in Sentences (1) and (4) shall have a flame-spread rating not more than 25.

(6)  The flame-spread rating limits specified in Sentence (5) do not apply to a corridor in which the flame-spread rating is not more than 150 provided the floor area is sprinklered.

3.1.13.7.  High Buildings

(1)  Except as permitted by Sentences (2) and (3), the interior wall, ceiling and floor finishes in a building regulated by the provisions of Subsection 3.2.6. shall conform to the flame-spread rating requirements in Articles 3.1.13.2. to 3.1.13.6. and to the flame-spread rating and smoke developed classification values in Table 3.1.13.7.

(2)  Except for a building of Group B major occupancy and elevator cars, the flame-spread rating and smoke developed classification of interior wall, floor and ceiling finishes need not conform to the values in Table 3.1.13.7., provided the building is sprinklered and the sprinkler system is electrically supervised in conformance with Sentence 3.2.6.4.(1).

(3)  Trim, millwork and doors in an exit stairway, a vestibule to an exit stairway, a lobby described in Sentence 3.4.4.2.(2), or a corridor not within a suite need not conform to the flame-spread rating and smoke developed classification requirements of Sentence (1) provided they have,

(a)	a flame-spread rating not more than 150,

(b)	a smoke developed classification not more than 300, and

(c)	an aggregate area not more than 10% of the area of the wall or ceiling on which they occur.

Table 3.1.13.7.
Flame-Spread Rating and Smoke Developed Classification in a High Building

Forming Part of Sentence 3.1.13.7.(1)

| Column 1 | Column 2 | Column 3 | Column 4 | Column 5 | Column 6 | Column 7 |
| --- | --- | --- | --- | --- | --- | --- |
| Location or Element | Maximum Flame-Spread Rating |  |  | Maximum Smoke Developed Classification |  |  |
|  | Wall Surface | Ceiling Surface (1) | Floor Surface | Wall Surface | Ceiling Surface (1) | Floor Surface |
| Exit stairways, vestibules to exit stairs and lobbies described in Sentence 3.4.4.2.(2) | 25 | 25 | 25 | 50 | 50 | 50 |
| Corridors not within suites | (2) | (2) | 300 | 100 | 50 | 500 |
| Elevator cars and vestibules | 25 | 25 | 300 | 100 | 100 | 300 |
| Service spaces and service rooms | 25 | 25 | 25 | 50 | 50 | 50 |
| Other locations and elements | (2) | (2) | No limit | 300 | 50 | No limit |

Note to Table 3.1.13.7.:

(1) See Sentence 3.1.13.4.(1) for lighting elements.

(2) Other requirements of this Part apply.

(4)  Except as permitted in Sentences (5) to (7), plumbing fixtures in a building regulated by the provisions of Subsection 3.2.6. shall have a smoke developed classification not more than 300.

(5)  A plumbing fixture that is not located in a Group B occupancy need not comply with Sentence (4) if the building is sprinklered.

(6)  A plumbing fixture may have a smoke developed classification more than 300 but not more than 500 if,

(a)	it is in a room where the wall surfaces have a smoke developed classification not more than 200, and

(b)	it is located in,

(i)	a Group C occupancy, or

(ii)	a Group B occupancy and the building is sprinklered.

(7)  A therapeutic bathing system in a Group B occupancy need not comply with Sentence (4) if the room in which it is located,

(a)	does not open directly into patients’ or residents’ sleeping rooms, and

(b)	is sprinklered.

3.1.13.8.  Noncombustible Construction

(1)  In a building required to be of noncombustible construction,

(a)	the flame-spread ratings required by Subsection 3.1.5. shall apply in addition to the requirements in this Subsection, and

(b)	the flame-spread ratings for exits in this Subsection shall also apply to any surface in the exit that would be exposed by cutting through the material in any direction, except that this requirement does not apply to doors, heavy timber construction in a sprinklered building and fire-retardant treated wood.

3.1.13.9.  Underground Walkways

(1)  Except for paint, the interior wall and ceiling finishes of an underground walkway shall be of noncombustible materials.

3.1.13.10.  Exterior Exit Passageway

(1)  The wall and ceiling finishes of an exterior exit passageway that provides the only means of egress from the rooms or suites it serves, including the soffit beneath and the guard on the passageway, shall have a flame-spread rating not more than 25, except that a flame-spread rating not more than 150 is permitted for up to 10% of the total wall area and for up to 10% of the total ceiling area.

3.1.14.  Roof Assemblies

3.1.14.1.  Fire-Retardant Treated Wood Roof Systems

(1)  If a fire-retardant treated wood roof system is used to comply with the requirements of Subsection 3.2.2., the roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126-M, “Test for Fire Spread Under Roof-Deck Assemblies”.

(2)  Supports for the roof deck assembly referred to in Sentence (1) shall consist of,

(a)	fire-retardant treated wood,

(b)	heavy timber construction,

(c)	noncombustible construction, or

(d)	a combination of the items described in Clauses (a), (b) and (c).

3.1.14.2.  Metal Roof Deck Assemblies

(1)  Except as permitted by Sentence (2), a metal roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126-M, “Test for Fire Spread Under Roof-Deck Assemblies”, if,

(a)	it supports a combustible material above the deck that could propagate a fire beneath the roof deck assembly, and

(b)	the deck is used to comply with the requirements of Sentences 3.2.2.25.(2), 3.2.2.32.(2), 3.2.2.53.(2), 3.2.2.59.(2), 3.2.2.69.(2), and 3.2.2.76.(2) for noncombustible construction.

(2)  The requirements of Sentence (1) are waived provided,

(a)	the combustible material above the roof deck is protected by not less than 12.7 mm thick gypsum board, mechanically fastened to a supporting assembly if located beneath the roof deck, or by a thermal barrier conforming to one of Clauses 3.1.5.12.(2)(c) to (e) that is located,

(i)	on the underside of the combustible material, or

(ii)	beneath the roof deck,

(b)	the building is sprinklered, or

(c)	the roof assembly has a fire-resistance rating not less than 45 min.

3.1.15.  Roof Covering

3.1.15.1.  Roof Covering Classification

(1)  A roof covering classification shall be determined in conformance with CAN/ULC-S107-M, “Fire Tests of Roof Coverings”.

3.1.15.2.  Roof Coverings

(1)  Except as permitted by Sentence (2), every roof covering shall have a Class A, B or C classification as determined in accordance with Article 3.1.15.1.

(2)  A roof covering is not required to have a Class A, B or C classification for

(a)	a tent,

(b)	an air-supported structure, or

(c)	a building of Group A, Division 2 occupancy not more than 2 storeys in building height and not more than 1 000 m2 in building area provided the roof covering is underlaid with noncombustible material.

3.1.16.  Fabrics

3.1.16.1.  Fabric Awnings, Canopies and Marquees

(1)  Fabrics used as part of an awning, canopy or marquee that is located within or attached to a building of any type of construction shall conform to CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films”.

3.1.17.  Occupant Load

3.1.17.1.  Occupant Load Determination

(1)  The occupant load of a floor area or part of a floor area, or of a building or part of a building not having a floor area, shall be based on,

(a)	the number of seats in an assembly occupancy having fixed seats,

(b)	2 persons per sleeping room or sleeping area in a dwelling unit or suite, or

(c)	the number of persons,

(i)	for which the area is designed, or

(ii)	determined from Table 3.1.17.1. for occupancies other than those described in Clauses (a) and (b).

(2)  If a floor area or part of it has been designed for an occupant load other than that determined from Table 3.1.17.1., a permanent sign indicating that occupant load shall be posted in a conspicuous location.

Table 3.1.17.1.
Occupant Load

Forming Part of Article 3.1.17.1.

| Column 1 | Column 2 |
| --- | --- |
| Type of Use of Building or Floor Area or Part of Floor Area | Area per Person, m2 |
| Assembly uses |  |
| space with fixed seats | See Clause (1)(a) |
| space with nonfixed seats | 0.75 |
| stages for theatrical performances | 0.75 |
| space with nonfixed seats and tables | 0.95 |
| standing space | 0.40 |
| stadia and grandstands | 0.60 |
| bowling alleys, pool and billiard rooms | 9.30 |
| classrooms | 1.85 |
| school shops and vocational rooms | 9.30 |
| reading or writing rooms or lounges | 1.85 |
| dining, alcoholic beverage and cafeteria space | 1.10 |
| laboratories in schools | 4.60 |
| exhibition halls other than those classified in Group E | 2.80 |
| Care or detention uses |  |
| B-1 : detention quarters | 11.60 |
| B-2 : treatment and sleeping room areas | 10.00 |
| B-3 : sleeping room areas | 10.00 |
| (See also Article 3.7.1.3.) |  |
| Residential uses |  |
| dwelling units | See Clause (1)(b) |
| dormitories | 4.60 |
| Business and personal services uses |  |
| personal service shops | 4.60 |
| offices | 9.30 |
| Mercantile uses |  |
| basements and first storeys | 3.70 |
| second storeys having a principal entrance from a pedestrian | 3.70 |
| thoroughfare or a parking area |  |
| dining, alcoholic beverage and cafeteria space | 1.10 |
| other storeys | 5.60 |
| Industrial uses |  |
| manufacturing or process rooms | 4.60 |
| storage garages | 46.00 |
| storage spaces (warehouse) | 28.00 |
| aircraft hangars | 46.00 |
| Other uses |  |
| cleaning and repair of goods | 4.60 |
| kitchens | 9.30 |
| storage | 46.00 |
| public corridors intended for occupancies in addition to pedestrian travel | 3.70 |

(3)  For the purposes of this Article, mezzanines, tiers and balconies shall be regarded as part of the floor area.

(4)  If a room or group of rooms is intended for different occupancies at different times, the value to be used from Table 3.1.17.1. shall be the value that gives the greatest number of persons for the occupancies concerned.

(5)  Except as provided by Sentence (6) or (7), in dining, alcoholic beverage and cafeteria spaces the occupant load shall be determined from Table 3.1.17.1.

(6)  The occupant load in Sentence (5) is permitted to be the number of persons for which the space is designed.

(7)  The occupant load in Sentence (6) shall be not more than that determined by using an area of 0.6 m2 per person.

3.1.17.2.  Dance Floor

(1)  The occupant load of a room in which a dance floor is situated shall be calculated in respect of that portion of the room that is not occupied by the dance floor.

3.1.17.3.  Public Pools

(1)  The occupant load of a public pool, except a wave action pool, shall be determined by the following formula:

occupant load = D2.5 + S1.4

where,

D =	the water surface area in square metres of the part of the pool that is deeper than 1 350 mm; and

S =	the water surface area in square metres of the part of the pool that is 1 350 mm in depth or less.

(2)  The occupant load of a wave action pool shall be determined by the following formula:

occupant load = D2.5 + S1.1

where,

D =	the water surface area in square metres of the part of the pool where the still water depth is greater than 1 000 mm; and

S =	the water surface area in square metres of the part of the pool where the still water depth is 1 000 mm or less.

3.1.18.  Drainage and Grades

3.1.18.1.  Drainage

(1)  The building shall be located and the building site graded so that water will not accumulate at or near the building and will not adversely affect any adjacent properties.

3.1.19.  Above Ground Electrical Conductors

3.1.19.1.  Clearance to Buildings

(1)  Where a building is to be constructed in proximity to existing above ground electrical conductors of a voltage not less than 2.5 kV and not more than 46 kV,

(a)	the building shall not be located beneath the conductors, and

(b)	the horizontal clearance between the building and the maximum conductor swing shall be not less than 3 m.

(2)  Where a building is to be constructed in proximity to existing above ground electrical conductors of a voltage more than 46 kV, the clearances between the building and the conductors shall conform to the requirements of CAN/CSA-C22.3 No.1, “Overhead Systems”.

3.1.19.2. Exception

(1)  Article 3.1.19.1. does not apply to buildings containing electrical equipment and electrical installations used exclusively in the generation, transformation or transmission of electrical power or energy intended for sale or distribution to the public.

Section 3.2.  Building Fire Safety

3.2.1.  General

3.2.1.1.  Exceptions in Determining Building Height

(1)  A roof-top enclosure provided for elevator machinery, a stairway or a service room used for no purpose other than for service to the building, shall not be considered as a storey in calculating the building height.

(2)  Space under tiers of seats in a building of the arena type shall not be considered as adding to the building height provided the space is used only for dressing rooms, concession stands and similar purposes incidental to the major occupancy of the building.

(3)  Except as required by Sentence (5), the space above a mezzanine need not be considered as a storey in calculating building height provided,

(a)	the aggregate area of mezzanines that are not superimposed does not exceed 40% of the open area of the room in which they are located, and

(b)	except as permitted in Sentence (8) and Sentence 3.3.2.11.(3) the space above the mezzanine is used as an open area without partitions or subdividing walls higher than 1 070 mm above the mezzanine floor.

(4)  Except as required by Sentence (5), the space above a mezzanine need not be considered as a storey in calculating the building height provided,

(a)	the aggregate area of mezzanines that are not superimposed and do not meet the conditions of Sentence (3) does not exceed 10% of the floor area in which they are located, and

(b)	the area of mezzanine in a suite does not exceed 10% of the area of that suite.

(5)  Except as permitted by Sentences (6) and (7), each level of mezzanine that is partly or wholly superimposed above the first level of mezzanine shall be considered as a storey in calculating the building height.

(6)  Platforms intended solely for periodic inspection and elevated catwalks need not be considered as floor assemblies or mezzanines for the purpose of determining building height provided,

(a)	they are not used for storage,

(b)	they are constructed with noncombustible materials unless the building is permitted to be of combustible construction, and

(c)	where they are intended to be occupied, they have an occupant load of not more that 4 persons.

(7)  Mezzanines, elevated walkways and platforms that are intended to be occupied in Group F, Division 2 or 3 major occupancies need not be considered as storeys in calculating building height provided,

(a)	the building is of noncombustible construction, and

(b)	the occupant load is not more than 4 persons.

(8)  The space above a mezzanine conforming to Sentence (3) is permitted to include an enclosed space whose area does not exceed 10% of the open area of the room in which the mezzanine is located, provided the enclosed space does not obstruct visual communication between the open space above the mezzanine and the room in which it is located.

(9)  A service space in which facilities are included to permit a person to enter and to undertake maintenance and other operations pertaining to building services from within the service space need not be considered a storey if it conforms to Articles 3.2.5.15. and 3.3.1.23. and Sentences 3.2.4.19.(12), 3.2.7.3.(2), 3.3.1.3.(7), 3.4.2.4.(3) and 3.4.4.4.(9).

3.2.1.2.  Storage Garage Considered as a Separate Building

(1)  A basement used primarily as a storage garage is permitted to be considered as a separate building for the purposes of Subsection 3.2.2., provided the floor and roof assemblies above the basement and the exterior walls of the basement above the adjoining ground level are constructed as fire separations of masonry or concrete having a fire-resistance rating not less than 2 h, except as permitted by Sentence (2).

(2)  The exterior wall of a basement that is required to be a fire separation with a fire-resistance rating in accordance with Sentence (1) is permitted to be penetrated by openings that are not protected by closures provided,

(a)	the storage garage is sprinklered,

(b)	every opening in the exterior wall is separated from storeys above the opening by a projection of the floor or roof assembly above the basement, extending not less than,

(i)	1 000 mm beyond the exterior face of the storage garage if the upper storeys are required to be of noncombustible construction, or

(ii)	2 000 mm beyond the exterior face of the storage garage if the upper storeys are permitted to be of combustible construction, or

(c)	the exterior walls of any storeys located above the floor or roof assembly referred to in Sentence (1) are recessed behind the outer edge of the assembly by not less than,

(i)	1 000 mm if the upper storeys are required to be of noncombustible construction, or

(ii)	2 000 mm if the upper storeys are permitted to be of combustible construction.

(3)  The floor or roof assembly projection referred to in Clause (2)(b) shall have a fire-resistance rating not less than 2 h and shall have no openings within the projection.

3.2.1.3.  Roof Considered as a Wall

(1)  For the purposes of this Section any part of a roof that is pitched at an angle of 60 or more to the horizontal and is adjacent to a space intended for occupancy within a building shall be considered as part of an exterior wall of the building.

3.2.1.4.  Floor Assembly over Basement

(1)  Except as permitted by Sentence 3.2.2.42.(3), 3.2.2.43.(3), 3.2.2.45.(3), 3.2.2.46.(3), 3.2.2.47.(3) or 3.2.2.48.(3), a floor assembly immediately above a basement shall be constructed as a fire separation having a fire-resistance rating conforming to the requirements of Articles 3.2.2.20. to 3.2.2.83. for a floor assembly, but not less than 45 min.

(2)  All loadbearing walls, columns and arches supporting a floor assembly immediately above a basement shall have a fire-resistance rating not less than that required by Sentence (1) for the floor assembly.

3.2.1.5.  Fire Containment in Basements

(1)  Except as permitted by Sentences (2) and 3.2.2.15.(3), in a building in which an automatic sprinkler system is not required to be installed by Articles 3.2.2.20. to 3.2.2.83., every basement shall,

(a)	be sprinklered, or

(b)	be subdivided into fire compartments not more than 600 m2 in area by a fire separation having a fire-resistance rating not less than that required for the floor assembly immediately above the basement.

(2)  An open-air storey need not conform to Sentence (1).

3.2.1.6.  Mezzanines

(1)  The floor assembly of a mezzanine that is required to be considered as a storey in calculating building height shall be constructed in conformance with the fire separation requirements for floor assemblies in Articles 3.2.2.20. to 3.2.2.83.

3.2.2.  Building Size and Construction Relative to Occupancy

3.2.2.1.  Application

(1)  Except as permitted by Article 3.2.2.3., a building shall be constructed in conformance with this Subsection to prevent fire spread and collapse caused by the effects of fire.

3.2.2.2.  Special and Unusual Structures

(1)  A structure that cannot be identified with the characteristics of a building in Articles 3.2.2.20. to 3.2.2.83. shall be protected against fire spread and collapse in conformance with good fire protection engineering practice.

3.2.2.3.  Exceptions to Structural Fire Protection

(1)  Fire protection is not required for,

(a)	steel lintels above openings not more than 2 m wide in loadbearing walls and not more than 3 m wide in non-loadbearing walls,

(b)	steel lintels above openings more than 2 m wide in loadbearing walls and more than 3 m wide in non-loadbearing walls, provided the lintels are supported at intervals of not more than 2 m by structural members with the required fire-resistance rating,

(c)	the bottom flanges of shelf angles and plates that are not a part of the structural frame,

(d)	steel members for framework around elevator hoistway doorways, steel for the support of elevator and dumbwaiter guides, counterweights and other similar equipment, that are entirely enclosed in a hoistway and are not a part of the structural frame of the building,

(e)	steel members of stairways and escalators that are not a part of the structural frame of a building,

(f)	steel members of porches, exterior balconies, exterior stairways, fire escapes, cornices, marquees and other similar appurtenances, provided they are outside an exterior wall of a building, and

(g)	loadbearing steel or concrete members wholly or partly outside a building face in a building not more than 4 storeys in building height and classified as Group A, B, C, D or F, Division 3 major occupancy provided the members are,

(i)	not less than 1 000 mm away from any unprotected opening in an exterior wall, or

(ii)	shielded from heat radiation in the event of a fire within the building by construction that will provide the same degree of protection that would be necessary if the member was located inside the building, with the protection extending on either side of the member a distance equal to the projection of the member from the face of the wall.

3.2.2.4.  Buildings with Multiple Major Occupancies

(1)  The requirements restricting fire spread and collapse for a building of a single major occupancy classification are provided in this Subsection according to its building height and building area.

(2)  If a building contains more than one major occupancy, classified in more than one Group or Division, the requirements of this Subsection concerning building size and construction relative to major occupancy shall apply according to Articles 3.2.2.5. to 3.2.2.8.

3.2.2.5.  Applicable Building Height and Area

(1)  In determining the fire safety requirements of a building in relation to each of the major occupancies contained in it, the building height and building area of the entire building shall be used.

3.2.2.6.  Multiple Major Occupancies

(1)  Except as permitted by Articles 3.2.2.7. and 3.2.2.8., in a building containing more than one major occupancy, the requirements of this Subsection for the most restricted major occupancy contained shall apply to the whole building.

3.2.2.7.  Superimposed Major Occupancies

(1)  Except as permitted by Article 3.2.2.8., in a building in which one major occupancy is located entirely above another major occupancy, the requirements in this Subsection for each portion of the building containing a major occupancy shall apply to that portion as if the entire building was of that major occupancy.

(2)  If one major occupancy is located above another major occupancy, the fire-resistance rating of the floor assembly between the major occupancies shall be determined on the basis of the requirements of this Subsection for the lower major occupancy.

3.2.2.8.  Exceptions for Major Occupancies

(1)  In a building in which the aggregate area of all major occupancies in a particular Group or Division is not more than 10% of the floor area of the storey in which they are located, these major occupancies need not be considered as major occupancies for the purposes of this Subsection, provided they are not classified as Group F, Division 1 or 2 occupancies.

(2)  A helicopter landing area on the roof of a building need not be considered a major occupancy for purposes of Subsection 3.2.2. where such landing area is not more than 10% of the area of the roof.

3.2.2.9.  Crawl Spaces

(1)  For the purposes of Articles 3.2.1.4. and 3.2.1.5., a crawl space shall be considered as a basement if it is,

(a)	more than 1 800 mm high between the lowest part of the floor assembly and the ground or other surface below,

(b)	used for any occupancy,

(c)	used for the passage of flue pipes, or

(d)	used as a plenum in combustible construction.

(2)  A floor assembly immediately above a crawl space is not required to be constructed as a fire separation and is not required to have a fire-resistance rating provided the crawl space is not required to be considered as a basement by Sentence (1).

3.2.2.10.  Streets

(1)  Every building shall face a street located in conformance with the requirements of Articles 3.2.5.4 and 3.2.5.5 for access routes.

(2)  For the purposes of Subsections 3.2.2. and 3.2.5. an access route conforming to Subsection 3.2.5. is permitted to be considered as a street.

(3)  A building is considered to face 2 streets provided not less than 50% of the building perimeter is located within 15 m of the street or streets.

(4)  A building is considered to face 3 streets provided not less than 75% of the building perimeter is located within 15 m of the street or streets.

(5)  Enclosed spaces, tunnels, bridges and similar structures, even though used for vehicular or pedestrian traffic, are not considered as streets for the purpose of this Part.

3.2.2.11.  Exterior Balconies

(1)  An exterior balcony shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83., as applicable to the occupancy classification of the building.

3.2.2.12.  Exterior Passageways

(1)  An elevated exterior passageway used as part of a means of egress shall conform to the requirements of Articles 3.2.2.20. to 3.2.2.83. for mezzanines.

3.2.2.13.  Occupancy on Roof

(1)  A portion of a roof that supports an occupancy shall be constructed in conformance with the fire separation requirements of Articles 3.2.2.20. to 3.2.2.83. for floor assemblies.

3.2.2.14.  Roof-Top Enclosures

(1)  A roof-top enclosure for elevator machinery or for a service room shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83.

(2)  A roof-top enclosure for elevator machinery or for a service room, not more than one storey high, is not required to have a fire-resistance rating.

(3)  A roof-top enclosure for a stairway shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.83.

(4)  A roof-top enclosure for a stairway need not have a fire-resistance rating nor be constructed as a fire separation.

3.2.2.15.  Storeys below Ground

(1)  If a building is erected entirely below the adjoining finished ground level and does not extend more than one storey below that ground level, the minimum precautions against fire spread and collapse shall be the same as are required for basements under a building of 1 storey in building height having the same occupancy and building area.

(2)  If any portion of a building is erected entirely below the adjoining finished ground level and extends more than one storey below that ground level, the following minimum precautions against fire spread and collapse shall be taken:

(a)	except as permitted by Sentence (3), the basements shall be sprinklered,

(b)	a floor assembly below the ground level shall be constructed as a fire separation with a fire-resistance rating not less than,

(i)	3 h if the basements are intended for use as Group E or Group F, Division 1 or 2 occupancies, or

(ii)	2 h if the basements are not intended for use as Group E or Group F, Division 1 or 2 occupancies, and

(c)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the construction that they support.

(3)  If the first storey of a building is not required to be sprinklered, sprinklers are not required in the storey immediately below the first storey, provided the storey below,

(a)	contains only residential occupancies, and

(b)	has at least one unobstructed access opening conforming to Sentence 3.2.5.1.(2) installed on that storey for each 15 m of wall length in at least one wall required by this Subsection to face a street.

3.2.2.16.  Heavy Timber Roof Permitted

(1)  Unless otherwise permitted by Articles 3.2.2.20. to 3.2.2.83., a roof assembly in a building up to 2 storeys in building height is permitted to be of heavy timber construction regardless of building area or type of construction required, provided the building is sprinklered.

(2)  If Sentence (1) permits a roof assembly to be of heavy timber construction, structural members in the storey immediately below the roof assembly are permitted to be of heavy timber construction.

3.2.2.17.  Sprinklers in Lieu of Roof Rating

(1)  The requirements in Articles 3.2.2.20. to 3.2.2.83. for roof assemblies to have a fire-resistance rating are permitted to be waived provided,

(a)	the building is sprinklered,

(b)	the sprinkler system in Clause (a) is electrically supervised in conformance with Sentence 3.2.4.9.(2), and

(c)	the operation of the sprinkler system in Clause (a) will cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4).

3.2.2.18.  Automatic Sprinkler System Required

(1)  If an automatic sprinkler system is required by Articles 3.2.2.20. to 3.2.2.83., the system shall conform to the requirements of Articles 3.2.4.7., 3.2.4.8., 3.2.4.9. and 3.2.5.13.

3.2.2.19.  Buildings Containing Impeded Egress Zones

(1)  A building containing an impeded egress zone and conforming to the appropriate requirements of Articles 3.2.2.20. to 3.2.2.83. is not required to conform to the requirements of Articles 3.2.2.36. and 3.2.2.37. for a Group B, Division 1 major occupancy provided,

(a)	the building is sprinklered,

(b)	it is not more than 1 storey in building height,

(c)	it does not include,

(i)	a contained use area,

(ii)	sleeping accommodation,

(iii)	a high hazard industrial occupancy, or

(iv)	a mercantile occupancy,

(d)	the building area is not more than 6 400 m2 if the building includes a medium hazard industrial occupancy,

(e)	the impeded egress zone does not extend beyond the boundaries of the fire compartment in which it is located, and

(f)	the occupant load of the impeded egress zone is not more than 100.

3.2.2.20.  Group A, Division 1, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.21. and 3.2.2.22., a building classified as Group A, Division 1 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.21.  Group A, Division 1, One Storey, Limited Area

(1)  A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 1 storey in building height,

(b)	it has less than 40% of the area of the building as 2 storeys for the purpose of,

(i)	development of productions including preparation of scenery and costumes and rehearsal of performers,

(ii)	organization of performers, scenery and sound equipment,

(iii)	preparation by performers for a performance,

(iv)	managerial functions, or

(v)	toilets, rest rooms and similar public facilities,

(c)	it has no occupancy above or below the auditorium other than one that serves it or is dependent on it,

(d)	it is not more than 600 m2 in building area, and

(e)	the occupant load is not more than 600.

(2)  The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations,

(i)	with a fire-resistance rating not less than 45 min, or

(ii)	of heavy timber construction, and

(b)	loadbearing walls, columns and arches shall,

(i)	have a fire-resistance rating not less than that required for the supported assembly, or

(ii)	be of heavy timber construction.

3.2.2.22.  Group A, Division 1, One Storey

(1)  A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 1 storey in building height,

(b)	no part of an auditorium floor is more than 5 m above or below grade,

(c)	no occupancy is above or below the auditorium other than one that serves it or is dependent on it, and

(d)	the occupant load of the auditorium floor is not more than 300.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(e)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.23.  Group A, Division 2, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.24. to 3.2.2.28., a building classified as Group A, Division 2 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.24.  Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered

(1)  A building classified as Group A, Division 2, that is not limited by building area, is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered, and

(b)	it is not more than 6 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.25.  Group A, Division 2, up to 2 Storeys

(1)  A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.25.

Table 3.2.2.25.
Maximum Building Area, Group A, Division 2, up to 2 Storeys

Forming Part of Sentence 3.2.2.25.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 600 | 2 000 | 2 400 |
| 2 | 800 | 1 000 | 1 200 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than,

(i)	800 m2 if facing one street,

(ii)	1 000 m2 if facing 2 streets, or

(iii)	1 200 m2 if facing 3 streets, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.26.  Group A, Division 2, up to 2 Storeys, Increased Area, Sprinklered

(1)  A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	4 800 m2 if 1 storey in building height, or

(ii)	2 400 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less 45 min, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.27.  Group A, Division 2, up to 2 Storeys, Sprinklered

(1)  A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	2 400 m2 if 1 storey in building height with no basement,

(ii)	1 200 m2 if 1 storey in building height, or

(iii)	600 m2 if 2 storeys in building height.

3.2.2.28.  Group A, Division 2, One Storey

(1)  A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided,

(a)	it is not more than 1 storey in building height, and

(b)	except as permitted by Sentence (2), it has a building area not more than,

(i)	400 m2 if facing one street,

(ii)	500 m2 if facing 2 streets, or

(iii)	600 m2 if facing 3 streets.

(2)  In a building referred to in Sentence (1) without a basement, the building area limits of Sentence (1) are permitted to be doubled provided a fire separation with a fire-resistance rating not less than 1 h is used to separate the building into fire compartments, each one of which does not exceed the area limits of Clause 1(b).

3.2.2.29.  Group A, Division 3, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.30. to 3.2.2.34., a building classified as Group A, Division 3 shall conform to Sentences (2) and (3).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6.,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less than 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  If intended for occasional use for trade shows and similar exhibition purposes, the building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered.

3.2.2.30.  Group A, Division 3, up to 2 Storeys

(1)  A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.30.

Table 3.2.2.30.
Maximum Building Area, Group A, Division 3, up to 2 Storeys

Forming Part of Sentence 3.2.2.30.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 000 | 5 000 | 6 000 |
| 2 | 2 000 | 2 500 | 3 000 |

(2)  Except as permitted by Clauses (c) and (d), the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of heavy timber construction, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches and structural members within the storey immediately below a roof assembly are permitted to be of heavy timber construction.

(3)  If intended for occasional use for trade shows and similar exhibition purposes, the building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered.

3.2.2.31.  Group A, Division 3, up to 2 Storeys, Sprinklered

(1)  A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	12 000 m2 if 1 storey in building height, or

(ii)	6 000 m2 if 2 storeys in building height.

(2)  Except as permitted by Clause (c) and Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches are permitted to be of heavy timber construction.

3.2.2.32.  Group A, Division 3, One Storey, Increased Area

(1)  A building classified as Group A, Division 3 is permitted to conform to Sentences (2) and (3) provided,

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area not more than,

(i)	2 400 m2 if facing one street,

(ii)	3 000 m2 if facing 2 streets, or

(iii)	3 600 m2 if facing 3 streets.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(b)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than,

(i)	1 200 m2 if facing one street,

(ii)	1 500 m2 if facing 2 streets, or

(iii)	1 800 m2 if facing 3 streets, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

(3)  If intended for occasional use for trade shows and similar exhibition purposes, the building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered.

3.2.2.33.  Group A, Division 3, One Storey, Sprinklered

(1)  A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 1 storey in building height, and

(c)	it has a building area not more than 7 200 m2.

3.2.2.34.  Group A, Division 3, One Storey

(1)  A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided,

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area not more than,

(i)	1 000 m2 if facing one street,

(ii)	1 250 m2 if facing 2 streets, or

(iii)	1 500 m2 if facing 3 streets.

3.2.2.35.  Group A, Division 4

(1)  Except as permitted by Sentences (2) and (3), a building classified as Group A, Division 4 shall be of noncombustible construction.

(2)  Roof assemblies and supporting arches and columns are permitted to be of heavy timber construction.

(3)  A building classified as Group A, Division 4 is permitted to be of combustible construction provided,

(a)	the occupant load is less than 1 500, and

(b)	the building has a limiting distance not less than 6 m.

(4)  Sprinklers shall be installed in all spaces below tiers of seats in a building classified as Group A, Division 4 if those spaces are used for occupancy.

3.2.2.36.  Group B, Division 1, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Article 3.2.2.37., a building classified as Group B, Division 1 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.37.  Group B, Division 1, up to 3 Storeys, Sprinklered

(1)  A building classified as Group B, Division 1 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1) the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area,

(i)	that is not limited if the building is not more than 1 storey in building height,

(ii)	not more than 12 000 m2 if 2 storeys in building height, or

(iii)	not more than 8 000 m2 if 3 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.38.  Group B, Division 2 or Division 3, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.39. to 3.2.2.41., a building classified as Group B, Division 2 or Division 3 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.39.  Group B, Division 2 or Division 3, up to 3 Storeys, Sprinklered

(1)  A building classified as Group B, Division 2 or Division 3 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area,

(i)	that is not limited if the building is not more than 1 storey in building height,

(ii)	not more than 12 000 m2 if 2 storeys in building height, or

(iii)	not more than 8 000 m2 if 3 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.40.  Group B, Division 2 or Division 3, up to 2 Storeys, Sprinklered

(1)  A building classified as Group B, Division 2 or Division 3 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	2 400 m2 if 1 storey in building height, or

(ii)	1 600 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.41.  Group B, Division 2 or Division 3, One Storey, Sprinklered

(1)  A building classified as Group B, Division 2 or Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination, provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 1 storey in building height, and

(c)	it has a building area not more than 500 m2.

3.2.2.42.  Group C, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.43. to 3.2.2.48., a building classified as Group C shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	Reserved

(b)	except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

3.2.2.43.  Group C, up to 6 Storeys

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided,

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.43.A. or Table 3.2.2.43.B.

(2)  The building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating of not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating of not less than 1 h,

(c)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

Table 3.2.2.43.A.
Maximum Building Area, Group C, up to 6 Storeys

Forming Part of Sentence 3.2.2.43.(1)

| Column 1 | Column 2 |  | Column 3 | Column 4 |  |
| --- | --- | --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |  |  |
|  | Facing 1 Street | Facing 2 Streets |  |  | Facing 3 Streets |
| 1 | unlimited | unlimited |  |  | unlimited |
| 2 | 6 000 | unlimited |  |  | unlimited |
| 3 | 4 000 | 5 000 |  |  | 6 000 |
| 4 | 3 000 | 3 750 |  |  | 4 500 |
| 5 | 2 400 | 3 000 |  |  | 3 600 |
| 6 | 2 000 | 2 500 |  |  | 3 000 |

Table 3.2.2.43.B.
Maximum Building Area, Group C up to 6 Storeys, Sprinklered

Forming Part of Sentence 3.2.2.43.(1)

| Column 1 | Column 2 |
| --- | --- |
| No. of Storeys | Maximum Area, m2 |
| 1 | unlimited |
| 2 | unlimited |
| 3 | 12 000 |
| 4 | 9 000 |
| 5 | 7 200 |
| 6 | 6 000 |

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

3.2.2.44.  Reserved

3.2.2.45.  Group C, up to 4 Storeys, Sprinklered

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than,

(i)	7 200 m2 if 1 storey in building height,

(ii)	3 600 m2 if 2 storeys in building height,

(iii)	2 400 m2 if 3 storeys in building height, or

(iv)	1 800 m2 if 4 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.46.  Group C, up to 3 Storeys, Increased Area

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided,

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.46.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

Table 3.2.2.46.
Maximum Building Area, Group C up to 3 Storeys, Increased Area

Forming Part of Sentence 3.2.2.46.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 2 400 | 3 000 | 3 600 |
| 2 | 1 200 | 1 500 | 1 800 |
| 3 | 800 | 1 000 | 1 200 |

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.47.  Group C, up to 3 Storeys

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided,

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.47.

Table 3.2.2.47.
Maximum Building Area, Group C, up to 3 Storeys

Forming Part of Sentence 3.2.2.47.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 800 | 2 250 | 2 700 |
| 2 | 900 | 1 125 | 1 350 |
| 3 | 600 | 750 | 900 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.48.  Group C, up to 3 Storeys, Sprinklered

(1)  A building classified as Group C is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than,

(i)	5 400 m2 if 1 storey in building height,

(ii)	2 700 m2 if 2 storeys in building height, or

(iii)	1 800 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(3)  In a building that contains dwelling units that have more than 1 storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations.

(4)  In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.49.  Group D, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.50. to 3.2.2.56., a building classified as Group D shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6.,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.50.  Group D, up to 6 Storeys

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided,

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.50.

(2)  The building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

Table 3.2.2.50.
Maximum Building Area, Group D, up to 6 Storeys

Forming Part of Sentence 3.2.2.50.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | not limited | not limited | not limited |
| 2 | 7 200 | not limited | not limited |
| 3 | 4 800 | 6 000 | 7 200 |
| 4 | 3 600 | 4 500 | 5 400 |
| 5 | 2 800 | 3 600 | 4 320 |
| 6 | 2 400 | 3 000 | 3 600 |

3.2.2.51.  Group D, up to 6 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 6 storeys in building height, and

(c)	it has a building area,

(i)	that is not limited if the building is not more than 2 storeys in building height,

(ii)	not more than 14 400 m2 if 3 storeys in building height,

(iii)	not more than 10 800 m2 if 4 storeys in building height,

(iv)	not more than 8 640 m2 if 5 storeys in building height, or

(v)	not more than 7 200 m2 if 6 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.52.  Group D, up to 4 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than 3 600 m2.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.53.  Group D, up to 3 Storeys

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided,

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.53.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than,

(i)	2 400 m2 if facing one street,

(ii)	3 000 m2 if facing 2 streets, or

(iii)	3 600 m2 if facing 3 streets, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

Table 3.2.2.53.
Maximum Building Area, Group D, up to 3 Storeys

Forming Part of Sentence 3.2.2.53.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 800 | 6 000 | 7 200 |
| 2 | 2 400 | 3 000 | 3 600 |
| 3 | 1 600 | 2 000 | 2 400 |

3.2.2.54.  Group D, up to 3 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than,

(i)	14 400 m2 if 1 storey in building height,

(ii)	7 200 m2 if 2 storeys in building height, or

(iii)	4 800 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.55.  Group D, up to 2 Storeys

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided,

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.55.

Table 3.2.2.55.
Maximum Building Area, Group D, up to 2 Storeys

Forming Part of Sentence 3.2.2.55.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 800 | 1 000) | 1 200 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.56.  Group D, up to 2 Storeys, Sprinklered

(1)  A building classified as Group D is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	3 000 m2 if 1 storey in building height, or

(ii)	2 400 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.57.  Group E, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.58. to 3.2.2.62., a building classified as Group E shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.58.  Group E, up to 4 Storeys, Sprinklered

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than 1 800 m2.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.59.  Group E, up to 3 Storeys

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided,

(a)	it is not more than 3 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.59.

Table 3.2.2.59.
Maximum Building Area, Group E, up to 3 Storeys

Forming Part of Sentence 3.2.2.59.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 500 | 1 500 | 1 500 |
| 2 | 1 200 | 1 500 | 1 500 |
| 3 | 800 | 1 000 | 1 500 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is of noncombustible construction or is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1.,

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(e)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.60.  Group E, up to 3 Storeys, Sprinklered

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than,

(i)	7 200 m2 if 1 storey in building height,

(ii)	3 600 m2 if 2 storeys in building height, or

(iii)	2 400 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(d)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.61.  Group E, up to 2 Storeys

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided,

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.61.

Table 3.2.2.61.
Maximum Building Area, Group E, up to 2 Storeys

Forming Part of Sentence 3.2.2.61.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 600 | 750 | 900 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.62.  Group E, up to 2 Storeys, Sprinklered

(1)  A building classified as Group E is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	3 000 m2 if 1 storey in building height, or

(ii)	1 800 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.63.  Group F, Division 1, up to 4 Storeys, Sprinklered

(1)  Except as permitted by Articles 3.2.2.64. to 3.2.2.66., a building classified as Group F, Division 1 shall conform to Sentence (2) provided,

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than,

(i)	9 000 m2 if 1 storey in building height,

(ii)	4 500 m2 if 2 storeys in building height,

(iii)	3 000 m2 if 3 storeys in building height, or

(iv)	2 250 m2 if 4 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.64.  Group F, Division 1, up to 3 Storeys, Sprinklered

(1)  A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 3 storeys in building height, and

(c)	it has a building area not more than,

(i)	3 600 m2 if 1 storey in building height,

(ii)	1 800 m2 if 2 storeys in building height, or

(iii)	1 200 m2 if 3 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.65.  Group F, Division 1, up to 2 Storeys, Sprinklered

(1)  A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	2 400 m2 if 1 storey in building height, or

(ii)	1 200 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.66.  Group F, Division 1, One Storey

(1)  A building classified as Group F, Division 1 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided,

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area not more than 800 m2.

3.2.2.67.  Group F, Division 2, Any Height, Any Area, Sprinklered

(1)  Except as permitted by Articles 3.2.2.68. to 3.2.2.72., a building classified as Group F, Division 2 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(c)	mezzanines shall have a fire-resistance rating not less 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.68.  Group F, Division 2, up to 6 Storeys

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.68.A. or Table 3.2.2.68.B.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

Table 3.2.2.68.A.
Maximum Building Area, Group F, Division 2, up to 6 Storeys

Forming Part of Sentence 3.2.2.68.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 9 000 | 11 250 | 13 500 |
| 2 | 4 500 | 5 625 | 6 750 |
| 3 | 3 000 | 3 750 | 4 500 |
| 4 | 2 250 | 2 810 | 3 375 |
| 5 | 1 800 | 2 250 | 2 700 |
| 6 | 1 500 | 1 875 | 2 250 |

Table 3.2.2.68.B.
Maximum Building Area, Group F, Division 2, up to 6 Storeys, Sprinklered

Forming Part of Sentence 3.2.2.68.(1)

| Column 1 | Column 2 |
| --- | --- |
| No. of Storeys | Maximum Area, m2 |
| 1 | 27 000 |
| 2 | 13 500 |
| 3 | 9 000 |
| 4 | 6 750 |
| 5 | 5 400 |
| 6 | 4 500 |

3.2.2.69.  Group F, Division 2, up to 4 Storeys, Increased Area

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.69.A. or Table 3.2.2.69.B.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

Table 3.2.2.69.A.
Maximum Building Area, Group F, Division 2, up to 4 Storeys, Increased Area

Forming Part of Sentence 3.2.2.69.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 6 000 | 7 500 | 9 000 |
| 2 | 3 000 | 3 750 | 4 500 |
| 3 | 2 000 | 2 500 | 3 000 |
| 4 | 1 500 | 1 875 | 2 250 |

Table 3.2.2.69.B.
Maximum Building Area, Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered

Forming Part of Sentence 3.2.2.69.(1)

| Column 1 | Column 2 |
| --- | --- |
| No. of Storeys | Maximum Area, m2 |
| 1 | 18 000 |
| 2 | 9 000 |
| 3 | 6 000 |
| 4 | 4 500 |

3.2.2.70.  Group F, Division 2, up to 4 Storeys

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.70.A. or Table 3.2.2.70.B.

(2)  The building referred to in Sentence (1) shall be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	if the building is not sprinklered, roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in buildings not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than,

(i)	1 600 m2 if facing 1 street,

(ii)	2 000 m2 if facing 2 streets, or

(iii)	2 400 m2 if facing 3 streets,

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction, and

(e)	loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the supported assembly.

Table 3.2.2.70.A.
Maximum Building Area, Group F, Division 2, up to 4 Storeys

Forming Part of Sentence 3.2.2.70.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 3 200 | 4 000 | 4 800 |
| 2 | 1 600 | 2 000 | 2 400 |
| 3 | 1 070 | 1 340 | 1 600 |
| 4 | 800 | 1 000 | 1 200 |

Table 3.2.2.70.B.
Maximum Building Area, Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered

Forming Part of Sentence 3.2.2.70.(1)

| Column 1 | Column 2 |
| --- | --- |
| No. of Storeys | Maximum Area, m2 |
| 1 | 9 600 |
| 2 | 4 800 |
| 3 | 3 200 |
| 4 | 2 400 |

3.2.2.71.  Group F, Division 2, up to 2 Storeys

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.71.

Table 3.2.2.71.
Maximum Building Area, Group F, Division 2, up to 2 Storeys

Forming Part of Sentence 3.2.2.71.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 600 | 750 | 900 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.72.  Group F, Division 2, up to 2 Storeys, Sprinklered

(1)  A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	4 500 m2 if 1 storey in building height, or

(ii)	1 800 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.73.  Group F, Division 3, Any Height, Any Area

(1)  Except as permitted by Articles 3.2.2.74. to 3.2.2.83., a building classified as Group F, Division 3 shall conform to Sentence (2).

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building shall be sprinklered if it is regulated by Subsection 3.2.6.,

(b)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, except that floor assemblies are permitted to be fire separations with a fire-resistance rating not less than 1 h in a storage garage with all storeys constructed as open-air storeys,

(c)	mezzanines shall have a fire-resistance rating not less 1 h,

(d)	if the building is not sprinklered, roof assemblies shall have a fire-resistance rating not less than 1 h, and

(e)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.74.  Group F, Division 3, up to 6 Storeys

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 6 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.74.

(2)  The building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

Table 3.2.2.74.
Maximum Building Area, Group F, Division 3, up to 6 Storeys

Forming Part of Sentence 3.2.2.74.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | not limited | not limited | not limited |
| 2 | 7 200 | 9 000 | 10 800 |
| 3 | 4 800 | 6 000 | 7 200 |
| 4 | 3 600 | 4 500 | 5 400 |
| 5 | 2 880 | 3 600 | 4 320 |
| 6 | 2 400 | 3 000 | 3 600 |

3.2.2.75.  Group F, Division 3, up to 6 Storeys, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 6 storeys in building height, and

(c)	it has a building area,

(i)	that is not limited if the building is not more than 1 storey in building height,

(ii)	not more than 21 600 m2 if 2 storeys in building height,

(iii)	not more than 14 400 m2 if 3 storeys in building height,

(iv)	not more than 10 800 m2 if 4 storeys in building height,

(v)	not more than 8 640 m2 if 5 storeys in building height, or

(vi)	not more than 7 200 m2 if 6 storeys in building height.

(2)  Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h, and

(c)	loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.76.  Group F, Division 3, up to 4 Storeys

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 4 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.76.

Table 3.2.2.76.
Maximum Building Area, Group F, Division 3, up to 4 Storeys

Forming Part of Sentence 3.2.2.76.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 800 | 6 000 | 7 200 |
| 2 | 2 400 | 3 000 | 3 600 |
| 3 | 1 600 | 2 000 | 2 400 |
| 4 | 1 200 | 1 500 | 1 800 |

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

(c)	roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than,

(i)	2 400 m2 if facing 1 street,

(ii)	3 000 m2 if facing 2 streets, or

(iii)	3 600 m2 if facing 3 streets, and

(d)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.77.  Group F, Division 3, up to 4 Storeys, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 4 storeys in building height, and

(c)	it has a building area not more than,

(i)	14 400 m2 if 1 storey in building height,

(ii)	7 200 m2 if 2 storeys in building height,

(iii)	4 800 m2 if 3 storeys in building height, or

(iv)	3 600 m2 if 4 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

(c)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.78.  Group F, Division 3, up to 2 Storeys

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided,

(a)	it is not more than 2 storeys in building height, and

(b)	it has a building area not more than the value in Table 3.2.2.78.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

Table 3.2.2.78.
Maximum Building Area, Group F, Division 3, up to 2 Storeys

Forming Part of Sentence 3.2.2.78.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| No. of Storeys | Maximum Area, m2 |  |  |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 600 | 2 000 | 2 400 |
| 2 | 800 | 1 000 | 1 200 |

3.2.2.79.  Group F, Division 3, up to 2 Storeys, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 2 storeys in building height, and

(c)	it has a building area not more than,

(i)	7 200 m2 if 1 storey in building height, or

(ii)	2 400 m2 if 2 storeys in building height.

(2)  The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and,

(a)	floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

(b)	loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall,

(i)	have a fire-resistance rating not less than 45 min, or

(ii)	be of noncombustible construction.

3.2.2.80.  Group F, Division 3, One Storey

(1)  A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided,

(a)	it is not more than 1 storey in building height, and

(b)	it has a building area is not more than,

(i)	5 600 m2 if facing 1 street,

(ii)	7 000 m2 if facing 2 streets, or

(iii)	8 400 m2 if facing 3 streets.

3.2.2.81.  Group F, Division 3, One Storey, Sprinklered

(1)  A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided,

(a)	except as permitted by Sentence 3.2.2.7.(1), the building is sprinklered,

(b)	it is not more than 1 storey in building height, and

(c)	it has a building area not more than 16 800 m2.

3.2.2.82.  Group F, Division 3, One Storey, Any Area, Low Fire Load Occupancy

(1)  A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided it is,

(a)	not more than 1 storey in building height,

(b)	used solely for low fire load occupancies such as,

(i)	power generating plants, or

(ii)	plants for the manufacture or storage of noncombustible materials, and

(c)	not limited in building area.

(2)  The building referred to in Sentence (1) shall be of noncombustible construction.

3.2.2.83.  Group F, Division 3, Storage Garages up to 22 m High

(1)  A building used as a storage garage with all storeys constructed as open-air storeys and having no other occupancy above it is permitted to have its floor, wall, ceiling and roof assemblies constructed without a fire-resistance rating provided it is,

(a)	of noncombustible construction,

(b)	not more than 22 m high, measured between grade and the ceiling level of the top storey,

(c)	not more than 10 000 m2 in building area, and

(d)	designed so that every portion of each floor area is within 60 m of an exterior wall opening.

3.2.3.  Spatial Separation and Exposure Protection

3.2.3.1.  Limiting Distance and Area of Unprotected Openings

(1)  Except as permitted by Articles 3.2.3.10. to 3.2.3.12., the area of unprotected openings in an exposing building face for the applicable limiting distance shall be not more than the value determined in accordance with,

(a)	Table 3.2.3.1.A. or Table 3.2.3.1.B. for an exposing building face conforming to Article 3.2.3.2. of a building or fire compartment that is not sprinklered, or

(b)	Table 3.2.3.1.C. or Table 3.2.3.1.D. for an exposing building face conforming to Article 3.2.3.2. of a sprinklered fire compartment that is part of a building that is sprinklered in conformance with Section 3.2.

(2)  The area of the unprotected openings in an exposing building face shall be the aggregate area of unprotected openings expressed as a percentage of the area of the exposing building face in Table 3.2.3.1.A., Table 3.2.3.1.B., Table 3.2.3.1.C. or Table 3.2.3.1.D.

(3)  For the purpose of determining the type of construction and cladding and the fire-resistance rating of an exterior wall,

(a)	the exposing building face shall be taken as the projection of the exterior wall onto a vertical plane located so that no portion of the exterior wall of the building or of a fire compartment, if the fire compartment complies with the requirements of Article 3.2.3.2., is between the vertical plane and the line to which the limiting distance is measured, and

(b)	the area of unprotected openings shall be determined from Table 3.2.3.1.A., Table 3.2.3.1.B., Table 3.2.3.1.C. or Table 3.2.3.1.D.

(4)  For the purpose of determining the actual percentage of unprotected openings permitted in an exterior wall, the location of the exposing building face is permitted to be taken at a vertical plane located so that there are no unprotected openings between the vertical plane and the line to which the limiting distance is measured.

(5)  If a building has any storey that is not sprinklered and fire fighting facilities cannot reach it within 10 min of the alarm being received, the required limiting distance shall be doubled.

(6)  If the surface temperature on the unexposed surface of a wall assembly exceeds the temperature limit of a standard fire test as permitted by Article 3.1.7.2., an allowance shall be made for the radiation from the hot unexposed wall surface by adding an equivalent area of unprotected opening to the area of actual openings as follows:

AC = A + (AF × FEO)

where,

AC =	corrected area of unprotected openings including actual and equivalent openings,

A =	actual area of unprotected openings,

AF =	area of exterior surface of the exposing building face, exclusive of openings, on which the temperature limit of the standard test is exceeded, and

FEO =	an equivalent opening factor derived from the following expression:

FEO =

where,

Tu =	average temperature in degrees Celsius of the unexposed wall surface at the time the required fire-resistance rating is reached under test conditions,

Te =	892°C for a fire-resistance rating not less than 45 min, 927°C for a fire-resistance rating not less than 1 h, and 1 010°C for a fire-resistance rating not less than 2 h.

(7)  Unless a closure used to protect an opening in an exposing building face has a protective performance equivalent to that required for the wall assembly in which it is located, an equivalent area of unprotected opening, determined in accordance with the procedures of Sentence (6) shall be added to the greater of,

(a)	the actual area of unprotected openings, or

(b)	the corrected area of unprotected openings.

Table 3.2.3.1.A.
Unprotected Opening Limits for a Building or Fire Compartment that is not Sprinklered

Forming Part of Article 3.2.3.1.

|  | Exposing Building Face |  | Area of Unprotected Openings for Groups A, C, D, and F, Division 3 Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Maximum Area, m2 | Ratio (L/H or H/L)(1) | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 0 | 1.2 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 18 | 20 | 25 | 30 | 35 | 40 | 45 | 50 |
| 1. | 10 | Less than 3:1 | 0 | 8 | 10 | 18 | 29 | 46 | 91 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 8 | 12 | 21 | 33 | 50 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 11 | 18 | 32 | 48 | 68 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. | 15 | Less than 3:1 | 0 | 7 | 9 | 14 | 22 | 33 | 63 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 8 | 10 | 17 | 25 | 37 | 67 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 10 | 15 | 26 | 39 | 53 | 87 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. | 20 | Less than 3:1 | 0 | 7 | 9 | 12 | 18 | 26 | 49 | 81 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 8 | 10 | 15 | 21 | 30 | 53 | 85 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 9 | 14 | 23 | 33 | 45 | 72 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. | 25 | Less than 3:1 | 0 | 7 | 8 | 11 | 16 | 23 | 41 | 66 | 98 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 8 | 9 | 13 | 19 | 26 | 45 | 70 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 9 | 13 | 21 | 30 | 39 | 62 | 90 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. | 30 | Less than 3:1 | 0 | 7 | 8 | 11 | 15 | 20 | 35 | 56 | 83 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 9 | 12 | 17 | 23 | 39 | 61 | 88 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 8 | 12 | 19 | 27 | 36 | 56 | 79 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6. | 40 | Less than 3:1 | 0 | 7 | 8 | 10 | 13 | 17 | 28 | 44 | 64 | 89 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 8 | 11 | 15 | 20 | 32 | 48 | 69 | 93 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 8 | 11 | 17 | 24 | 31 | 47 | 66 | 88 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7. | 50 | Less than 3:1 | 0 | 7 | 8 | 9 | 12 | 15 | 24 | 37 | 53 | 72 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 8 | 10 | 14 | 18 | 28 | 41 | 57 | 77 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 8 | 10 | 15 | 21 | 28 | 41 | 57 | 76 | 97 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8. | 60 | Less than 3:1 | 0 | 7 | 8 | 9 | 11 | 14 | 21 | 32 | 45 | 62 | 81 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 8 | 10 | 13 | 16 | 25 | 36 | 49 | 66 | 85 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 8 | 10 | 14 | 20 | 25 | 38 | 51 | 67 | 85 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9. | 80 | Less than 3:1 | 0 | 7 | 7 | 8 | 10 | 12 | 18 | 26 | 36 | 48 | 62 | 79 | 98 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 8 | 9 | 11 | 14 | 21 | 29 | 40 | 52 | 67 | 84 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 8 | 9 | 13 | 17 | 22 | 32 | 44 | 56 | 70 | 86 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10. | 100 | Less than 3:1 | 0 | 7 | 7 | 8 | 9 | 11 | 16 | 22 | 30 | 40 | 51 | 65 | 80 | 97 | 100 |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 8 | 9 | 11 | 13 | 18 | 25 | 34 | 44 | 56 | 69 | 84 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 7 | 9 | 12 | 16 | 20 | 29 | 39 | 49 | 61 | 74 | 89 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11. | 150 | Less than 3:1 | 0 | 7 | 7 | 8 | 9 | 10 | 13 | 17 | 22 | 29 | 37 | 46 | 56 | 67 | 79 | 93 | 100 |  |  |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 7 | 8 | 10 | 11 | 15 | 20 | 26 | 33 | 41 | 50 | 60 | 71 | 84 | 97 | 100 |  |  |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 7 | 8 | 11 | 13 | 17 | 24 | 31 | 39 | 48 | 57 | 68 | 79 | 91 | 100 |  |  |  |  |  |  |  |  |  |  |  |
| 12. | 250 | Less than 3:1 | 0 | 7 | 7 | 7 | 8 | 9 | 10 | 13 | 16 | 20 | 25 | 30 | 36 | 43 | 51 | 59 | 68 | 87 | 100 |  |  |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 7 | 8 | 9 | 10 | 12 | 15 | 19 | 24 | 28 | 34 | 40 | 47 | 55 | 63 | 72 | 92 | 100 |  |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 7 | 8 | 9 | 11 | 14 | 19 | 24 | 30 | 36 | 43 | 50 | 57 | 65 | 73 | 82 | 92 | 100 |  |  |  |  |  |  |  |  |
| 13. | 350 | Less than 3:1 | 0 | 7 | 7 | 7 | 8 | 8 | 9 | 11 | 14 | 16 | 20 | 24 | 28 | 33 | 38 | 44 | 50 | 64 | 81 | 99 | 100 |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 7 | 8 | 9 | 9 | 11 | 13 | 16 | 19 | 23 | 27 | 32 | 37 | 42 | 48 | 55 | 69 | 85 | 100 |  |  |  |  |  |  |
|  |  | over 10:1 | 0 | 7 | 8 | 9 | 10 | 12 | 16 | 21 | 25 | 30 | 36 | 41 | 47 | 53 | 59 | 66 | 73 | 88 | 100 |  |  |  |  |  |  |  |
| 14. | 500 | Less than 3:1 | 0 | 7 | 7 | 7 | 7 | 8 | 9 | 10 | 12 | 14 | 16 | 19 | 22 | 25 | 29 | 33 | 37 | 47 | 59 | 71 | 100 |  |  |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 7 | 7 | 8 | 8 | 10 | 12 | 14 | 16 | 19 | 22 | 25 | 29 | 33 | 37 | 41 | 52 | 63 | 76 | 100 |  |  |  |  |  |
|  |  | over 10:1 | 0 | 7 | 7 | 8 | 9 | 11 | 14 | 18 | 22 | 25 | 30 | 34 | 38 | 43 | 48 | 53 | 58 | 70 | 82 | 96 | 100 |  |  |  |  |  |
| 15. | 1 000 | Less than 3:1 | 0 | 7 | 7 | 7 | 7 | 7 | 8 | 9 | 9 | 10 | 12 | 13 | 14 | 16 | 18 | 20 | 22 | 27 | 33 | 39 | 58 | 82 | 100 |  |  |  |
|  |  | 3:1 to 10:1 | 0 | 7 | 7 | 7 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 15 | 17 | 19 | 21 | 23 | 26 | 31 | 37 | 43 | 63 | 86 | 100 |  |  |  |
|  |  | over 10:1 | 0 | 7 | 7 | 8 | 8 | 9 | 11 | 13 | 16 | 19 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 46 | 53 | 60 | 82 | 100 |  |  |  |  |
| 16. | 2 000 | Less than 3:1 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 17 | 20 | 23 | 33 | 44 | 58 | 74 | 93 | 100 |
|  |  | 3:1 to 10:1 | 0 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 20 | 23 | 27 | 37 | 49 | 63 | 79 | 97 | 100 |
|  |  | over 10:1 | 0 | 7 | 7 | 7 | 8 | 8 | 9 | 11 | 12 | 14 | 16 | 18 | 19 | 21 | 23 | 25 | 27 | 32 | 36 | 40 | 53 | 66 | 82 | 99 | 100 |  |

Insert regs\Graphics\Source Law\2006\350\350Table3.2.3.1.Bae.tif

Insert regs\Graphics\Source Law\2006\350\350Table3.2.3.1.Bbe.tif

Table 3.2.3.1.C.
Unprotected Opening Limits for a Building or Fire Compartment that is Sprinklered

Forming Part of Article 3.2.3.1.

| Exposing Building Face | Area of Unprotected Opening for Groups A, B, C, D and F, Division 3, Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Area, m2 | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 | 1.2 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| 10 | 0 | 16 | 24 | 42 | 66 | 100 |  |  |  |  |  |  |
| 15 | 0 | 16 | 20 | 34 | 50 | 74 | 100 |  |  |  |  |  |
| 20 | 0 | 16 | 20 | 30 | 42 | 60 | 100 |  |  |  |  |  |
| 25 | 0 | 16 | 18 | 26 | 38 | 52 | 90 | 100 |  |  |  |  |
| 30 | 0 | 14 | 18 | 24 | 34 | 46 | 78 | 100 |  |  |  |  |
| 40 | 0 | 14 | 16 | 22 | 30 | 40 | 64 | 96 | 100 |  |  |  |
| 50 | 0 | 14 | 16 | 20 | 28 | 36 | 56 | 82 | 100 |  |  |  |
| 60 | 0 | 14 | 16 | 20 | 26 | 32 | 50 | 72 | 98 | 100 |  |  |
| 80 | 0 | 14 | 16 | 18 | 22 | 28 | 42 | 58 | 80 | 100 |  |  |
| 100 | 0 | 14 | 16 | 18 | 22 | 26 | 36 | 50 | 68 | 88 | 100 |  |
| 150 or more | 0 | 14 | 14 | 16 | 20 | 22 | 30 | 40 | 52 | 66 | 82 | 100 |

Table 3.2.3.1.D.
Unprotected Opening Limits for a Building or Fire Compartment that is Sprinklered

Forming Part of Article 3.2.3.1.

| Exposing Building Face | Area of Unprotected Opening for Groups E and F, Division 1 and 2, Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Area, m2 | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 | 1.2 | 1.5 | 2 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| 10 | 0 | 8 | 12 | 20 | 34 | 50 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |
| 15 | 0 | 8 | 10 | 16 | 26 | 36 | 68 | 100 |  |  |  |  |  |  |  |  |  |  |
| 20 | 0 | 8 | 10 | 14 | 22 | 30 | 54 | 86 | 100 |  |  |  |  |  |  |  |  |  |
| 25 | 0 | 8 | 10 | 14 | 18 | 26 | 44 | 70 | 100 |  |  |  |  |  |  |  |  |  |
| 30 | 0 | 8 | 8 | 12 | 18 | 24 | 40 | 60 | 88 | 100 |  |  |  |  |  |  |  |  |
| 40 | 0 | 8 | 8 | 12 | 16 | 20 | 32 | 48 | 68 | 94 | 100 |  |  |  |  |  |  |  |
| 50 | 0 | 8 | 8 | 10 | 14 | 18 | 28 | 40 | 58 | 76 | 100 |  |  |  |  |  |  |  |
| 60 | 0 | 8 | 8 | 10 | 12 | 16 | 24 | 36 | 50 | 66 | 86 | 100 |  |  |  |  |  |  |
| 80 | 0 | 8 | 8 | 10 | 12 | 14 | 20 | 30 | 40 | 52 | 66 | 84 | 100 |  |  |  |  |  |
| 100 | 0 | 8 | 8 | 8 | 10 | 12 | 18 | 26 | 34 | 44 | 56 | 70 | 84 | 100 |  |  |  |  |
| 150 | 0 | 8 | 8 | 8 | 10 | 12 | 16 | 20 | 26 | 32 | 40 | 50 | 60 | 72 | 84 | 98 | 100 |  |
| 200 or more | 0 | 8 | 8 | 8 | 8 | 10 | 14 | 18 | 22 | 28 | 34 | 42 | 50 | 60 | 68 | 80 | 92 | 100 |

(8)  The required limiting distance for an exposing building face is permitted to be measured to a point beyond the property line that is not the centre line of a street, lane or public thoroughfare if,

(a)	the owners of the properties on which the limiting distance is measured and the municipality enter into an agreement in which such owners agree that,

(i)	each owner covenants that, for the benefit of land owned by the other covenantors, the owner will not construct a building on his or her property unless the limiting distance for exposing building faces in respect of the proposed construction is measured in accordance with the agreement,

(ii)	the covenants contained in the agreement are intended to run with the lands, and the agreement shall be binding on the parties and their respective heirs, executors, administrators, successors and assigns,

(iii)	the agreement shall not be amended or deleted from title without the consent of the municipality, and

(iv)	they will comply with such other conditions as the municipality considers necessary, including indemnification of the municipality by the other parties, and

(b)	the agreement referred to in Clause (a) is registered against the title of the properties to which it applies.

(9)  Where an agreement referred to in Sentence (8) is registered against the title of a property, the limiting distance for exposing building faces shall be measured to the point referred to in the agreement.

3.2.3.2.  Area of Exposing Building Face

(1)  Except as permitted by Sentences (2), and (3), the area of an exposing building face shall be calculated as the total area of exterior wall facing in one direction on any side of a building measured from the finished ground level to the uppermost ceiling.

(2)  If a building is divided by fire separations into fire compartments, the area of exposing building face is permitted to be calculated for each fire compartment provided the fire separations have a fire-resistance rating not less than 45 min.

(3)  In a building that contains an interconnected floor space, the area of the exposing building face for the interconnected floor space is permitted to be determined by considering each storey as a separate fire compartment notwithstanding openings through the floor assemblies.

3.2.3.3.  Wall Enclosing Attic or Roof Space

(1)  An exterior wall enclosing an attic or roof space and located above an exposing building face, shall be constructed in conformance with the requirements for the exposing building face.

3.2.3.4.  Reserved

3.2.3.5.  Wall with Limiting Distance Less Than 1.2 m

(1)  Openings in a wall that has a limiting distance less than 1.2 m shall be protected by closures whose fire-protection rating is in conformance with the fire-resistance rating required for the wall.

(2)  Wired glass or glass block shall not be used for a closure referred to in Sentence (1).

3.2.3.6.  Combustible Projections

(1)  Except for a building containing one or 2 dwelling units only, combustible projections on the exterior of a wall that could expose an adjacent building to fire spread and are more than 1 000 mm above ground level, including balconies, platforms, canopies, eave projections and stairs, shall not be permitted within,

(a)	1 200 mm of a property line or the centreline of a public way, or

(b)	2 400 mm of a combustible projection on another building on the same property.

3.2.3.7.  Construction of Exposing Building Face

(1)  Except as permitted by Articles 3.2.3.10. and 3.2.3.11, if a limiting distance shown in Table 3.2.3.1.A. or Table 3.2.3.1.C. for a Group A, B, C, D or Group F, Division 3 occupancy classification permits an exposing building face to have unprotected openings not more than 10% of the exposing building face, the exposing building face shall be,

(a)	of noncombustible construction having a fire-resistance rating not less than 1 h, and

(b)	clad with noncombustible cladding.

(2)  Except as permitted by Sentence (7) and Articles 3.2.3.10. and 3.2.3.11., if a limiting distance shown in Table 3.2.3.1.A. or Table 3.2.3.1.C. for a Group A, B, C, D or Group F, Division 3 occupancy classification permits an exposing building face to have unprotected openings more than 10% but not more than 25% of the exposing building face, the exposing building face shall,

(a)	have a fire-resistance rating not less than 1 h, and

(b)	be clad with noncombustible cladding.

(3)  Except as permitted by Articles 3.2.3.10. and 3.2.3.11., if a limiting distance shown in Table 3.2.3.1.A. or Table 3.2.3.1.C. for a Group A, B, C, D or Group F, Division 3 occupancy classification permits an exposing building face to have unprotected openings more than 25% but less than 100% of the exposing building face, the exposing building face shall have a fire-resistance rating not less than 45 min.

(4)  Except as permitted by Article 3.2.3.10., if a limiting distance shown in Table 3.2.3.1.B. or Table 3.2.3.1.D. for a Group E, or Group F, Division 1 or 2 occupancy classification permits an exposing building face to have unprotected openings not more than 10% of the exposing building face, the exposing building face shall be,

(a)	of noncombustible construction having a fire-resistance rating not less than 2 h, and

(b)	clad with noncombustible cladding.

(5)  Except as permitted by Sentence (7) and Article 3.2.3.10., if a limiting distance shown in Table 3.2.3.1.B. or Table 3.2.3.1.D. for a Group E, or Group F, Division 1 or 2 occupancy classification permits an exposing building face to have unprotected openings more than 10% but not more than 25% of the exposing building face, the exposing building face shall,

(a)	have a fire-resistance rating not less than 2 h, and

(b)	be clad with noncombustible cladding.

(6)  Except as permitted by Article 3.2.3.10., if a limiting distance shown in Table 3.2.3.1.B. or Table 3.2.3.1.D. for a Group E, or Group F, Division 1 or 2 occupancy classification permits an exposing building face to have unprotected openings more than 25% but less than 100% of the exposing building face, the exposing building face shall have a fire-resistance rating not less than 1 h.

(7)  The requirements of Clauses (2)(b) and (5)(b) are waived for a wall assembly that complies with the requirements of Article 3.1.5.5.

(8)  The construction requirements for the exposing building face that are required by Sentences (1) to (6) shall be satisfied before applying the increased opening area permitted by Sentence 3.2.3.12.(1).

3.2.3.8.  Protection of Exterior Building Face

(1)  Except as permitted by Sentence (3) and in addition to the requirements of Sentences 3.2.3.7.(2), (3), (5) and (6), foamed plastic insulation used in an exterior wall of a building more than 3 storeys in building height shall be protected on its exterior surface by,

(a)	concrete or masonry not less than 25 mm thick, or

(b)	noncombustible material that complies with the criteria for testing and conditions of acceptance of Sentence (2) when tested in conformance with CAN/ULC-S101-M, “Fire Endurance Tests of Building Construction and Materials”.

(2)  The criteria for testing and the conditions of acceptance for a wall assembly to satisfy the requirements of Clause (1)(b) are that,

(a)	the fire exposed area of the wall assembly shall be not less than 9.3 m2 and have no dimension less than 2 750 mm,

(b)	the exposed surface will include typical vertical and horizontal joints,

(c)	the test shall be continued for not less than 15 min and the standard time/temperature curve of the referenced standard shall be followed,

(d)	the noncombustible protective material will remain in place and no through openings will develop that are visible when viewed normal to the face of the material, and

(e)	the noncombustible protective material will not disintegrate in a manner that would permit fire to propagate along the surface of the test assembly.

(3)  The requirements of Sentence (1) are waived for wall assemblies that comply with the requirements of Article 3.1.5.5.

3.2.3.9.  Protection of Structural Members

(1)  Structural members, including beams, columns and arches, placed wholly or partly outside an exterior face of a building that are less than 3 m from the property line or centreline of a public thoroughfare shall be protected from exterior fire by fire protection having a fire-resistance rating not less than that required by Articles 3.2.2.20. to 3.2.2.83. for their protection from interior fires, but not less than 1 h.

(2)  Structural members of heavy timber construction, including beams, columns and arches, placed wholly or partly outside an exterior face of a building and 3 m or more from the property line or centreline of a public thoroughfare need not be covered with noncombustible cladding.

3.2.3.10.  Unlimited Unprotected Openings

(1)  An exposing building face of an open-air storey in a storage garage is permitted to have unlimited unprotected openings provided it has a limiting distance not less than 3 m.

(2)  The exposing building face of a storey that faces a street and is at the same level as the street is permitted to have unlimited unprotected openings if the limiting distance is not less than 9 m.

3.2.3.11.  Low Fire Load, One Storey Building

(1)  An exposing building face of a building of low hazard industrial occupancy conforming to Article 3.2.2.82. is permitted to be of noncombustible construction without a fire-resistance rating provided,

(a)	it is not a loadbearing wall, and

(b)	the limiting distance is not less than 3 m.

3.2.3.12.  Area Increase for Unprotected Openings

(1)  Except as required by Sentence 3.2.3.7.(8), the maximum area of unprotected openings in any exposing building face or fire compartment of a building that is not sprinklered is permitted to be doubled if the openings are glazed with,

(a)	glass block conforming to the requirements of Article 3.1.8.14., or

(b)	wired glass assemblies conforming to Supplementary Standard SB-2.

3.2.3.13.  Protection of Exit Facilities

(1)  Except as required by Sentence (3) and as permitted by Sentence 3.4.4.3.(1), if the plane of an exterior wall of an exit enclosure forms an angle less than 135 with the plane of an exterior wall of the building it serves, and an opening in the exterior wall of the exit enclosure could be exposed to fire from an opening in the exterior wall of the building, the opening in either the exterior wall of the exit or the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and,

(a)	less than 10 m below an opening in the exterior wall of the exit, or

(b)	less than 2 m above an opening in the exterior wall of the exit.

(2)  If an unenclosed exterior exit stair or ramp could be exposed to fire from an opening in the exterior wall of the building it serves, the opening in the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and,

(a)	less than 10 m below the exit stair or ramp, or

(b)	less than 5 m above the exit stair or ramp.

(3)  Except as permitted by Sentence 3.4.4.3.(1), if an exterior exit door in one fire compartment is within 3 m horizontally of an opening in another fire compartment and the exterior walls of these fire compartments intersect at an exterior angle of less than 135, the opening shall be protected in conformance with the requirements of Sentence (4).

(4)  The opening protection referred to in Sentences (1) to (3) shall consist of,

(a)	glass block conforming to the requirements of Article 3.1.8.14.,

(b)	a wired glass assembly conforming to Supplementary Standard SB-2, or

(c)	a closure conforming to the requirements of Subsection 3.1.8. and Articles 3.2.3.1. and 3.2.3.14.

3.2.3.14.  Wall Exposed to Another Wall

(1)  Except as required by Sentences (3) and 3.2.3.13.(1) or as permitted by Sentence 3.2.3.19.(4), if an unprotected opening in an exterior wall of a fire compartment is exposed to an unprotected opening in the exterior wall of another fire compartment, and the planes of the 2 walls are parallel or at an angle less than 135, measured from the exterior of the building, the unprotected openings in the 2 fire compartments shall be separated by a distance not less than DO,

where,

DO =	2D – [(θ/90) x D] but in no case less than 1 000 mm, and

D =	the greater required limiting distance for the exposing building faces of the 2 fire compartments, and

θ =	the angle made by the intersecting planes of the exposing building faces of the 2 fire compartments (in the case where the exterior walls are parallel and face each other, θ = 0).

(2)  The exterior wall of each fire compartment referred to in Sentence (1) within the distance, DO, shall have a fire-resistance rating not less than that required for the interior vertical fire separation between the fire compartment and the remainder of the building.

(3)  Sentence (1) does not apply to unprotected openings of fire compartments within a building that is sprinklered, but shall apply to,

(a)	unprotected openings of fire compartments on opposite sides of a firewall, and

(b)	exposure from unprotected openings of a fire compartment that is not protected by an automatic sprinkler system.

3.2.3.15.  Wall Exposed to Adjoining Roof

(1)  Except as permitted by Sentence 3.2.3.19.(4), if a wall in a building is exposed to a fire hazard from an adjoining roof of a separate fire compartment that is not sprinklered in the same building, and the exposed wall contains windows within 3 storeys vertically and 5 m horizontally of the roof, the roof shall contain no skylights within 5 m of the exposed wall.

3.2.3.16.  Protection of Soffits

(1)  Except as permitted by Sentences (2) and (3), where a common attic or roof space spans more than 2 suites of residential occupancy or more than 2 patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy, and the common attic or roof space projects beyond the exterior wall of the building, the portion of any soffit or other surface enclosing the projection that is less than 2 500 mm vertically above a window or door and less than 1 200 mm from either side of the window or door, shall have no openings and shall be protected by,

(a)	noncombustible material,

(i)	not less than 0.38 mm thick, and

(ii)	having a melting point not below 650°C,

(b)	not less than 12.7 mm thick gypsum soffit board or gypsum wallboard installed according to CSA A82.31-M, “Gypsum Board Application”,

(c)	not less than 11 mm thick plywood,

(d)	not less than 12.5 mm thick OSB or waferboard, or

(e)	not less than 11 mm thick lumber.

(2)  Where an attic or roof space, including its adjoining eave overhangs, is separated by construction conforming to Article 3.1.11.7. into compartments such that the resulting spaces are not common to more than 2 suites of residential occupancy or more than 2 patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy, the requirements in Sentence (1) do not apply.

(3)  If an eave overhang is completely separated from the remainder of the attic or roof space by fire stopping, the requirements of Sentence (1) do not apply.

(4)  The protection required by Sentence (1) for projections is permitted to be omitted if,

(a)	the fire compartments behind the window and door openings are sprinklered in accordance with Article 3.2.5.13., and

(b)	all rooms, including closets and bathrooms, having openings in the wall beneath the soffit are sprinklered, notwithstanding exceptions permitted in the standards referenced in Article 3.2.5.13. for the installation of automatic sprinkler systems.

3.2.3.17.  Canopy Protection for Vertically Separated Openings

(1)  Except as permitted by Sentences (2) and (3), if a storey classified as a Group E or Group F, Division 1 or 2 major occupancy is required to be separated from the storey above by a fire separation,

(a)	every opening in the exterior wall of the lower storey that is located vertically below an opening in the storey above shall be separated from the storey above by a canopy projecting not less than 1 000 mm from the face of the building at the intervening floor level, and

(b)	the canopy required by Clause (a) shall have a fire-resistance rating not less than that required for the floor assembly but need not be more than 1 h, except as required elsewhere in this Subsection.

(2)  Except as permitted by Sentence (3), the canopy required by Sentence (1) is permitted to be omitted if the exterior wall of the upper storey is recessed not less than 1 000 mm behind the exterior wall containing the opening in the lower storey.

(3)  The requirements of Sentences (1) and (2) are permitted to be waived if sprinklers are installed in,

(a)	the lower storey referred to in Clause (1)(a), and

(b)	the storey immediately above the lower storey.

3.2.3.18.  Covered Vehicular Passageway

(1)  A covered vehicular passageway designed as a receiving or shipping area shall be separated from every building or part of a building adjoining it by a fire separation having a fire-resistance rating not less than 1.5 h.

(2)  A covered vehicular passageway constructed below grade shall be of noncombustible construction.

3.2.3.19.  Walkway between Buildings

(1)  Except as required by Sentence 3.2.3.20.(2), if buildings are connected by a walkway, each building shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 45 min.

(2)  Except as permitted by Sentence (3), a walkway connected to a building required to be of noncombustible construction shall also be of noncombustible construction.

(3)  A walkway connected to a building required to be of noncombustible construction is permitted to be of heavy timber construction provided,

(a)	not less than 50% of the area of any enclosing perimeter walls is open to the outdoors, and

(b)	the walkway is at ground level.

(4)  A walkway of noncombustible construction used only as a pedestrian thoroughfare need not conform to the requirements of Articles 3.2.3.14. and 3.2.3.15.

(5)  A walkway between buildings shall be not more than 9 m wide.

3.2.3.20.  Underground Walkway

(1)  An underground walkway shall not be designed or used for any purpose other than pedestrian travel unless,

(a)	the purpose is permitted, and

(b)	sprinklers are installed in any space in the walkway containing an occupancy.

(2)  Buildings connected by an underground walkway shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 1 h.

(3)  An underground walkway shall be of noncombustible construction suitable for an underground location.

(4)  In an underground walkway,

(a)	smoke barrier doors shall be installed at intervals of not more than 100 m, or

(b)	the travel distance from the door of an adjacent room or space to the nearest exit shall be not more than one and a half times the least allowable travel distance to an exit for any of the adjacent occupancies as permitted by Sentence 3.4.2.5.(1).

(5)  An underground walkway between buildings shall be not more than 9 m wide.

3.2.4.  Fire Alarm and Detection Systems

3.2.4.1.  Determination of Requirement for a Fire Alarm System

(1)  Reserved

(2)  Except as permitted by Sentences (3) to (5) and Sentence 3.2.4.2.(4), a fire alarm system shall be installed in a building that contains,

(a)	a contained use area,

(b)	an impeded egress zone,

(c)	more than 3 storeys, including storeys below the first storey,

(d)	a total occupant load more than 300, other than in open air seating areas,

(e)	an occupant load more than 150 above or below the first storey, other than in open air seating areas,

(f)	a school, college, or child care facility, with an occupant load more than 40,

(g)	a licensed beverage establishment or a restaurant, with an occupant load more than 150,

(h)	a medium hazard industrial occupancy or a low hazard industrial occupancy with an occupant load more than 75 above or below the first storey,

(i)	a residential occupancy with sleeping accommodation for more than 10 persons,

(j)	a high hazard industrial occupancy with an occupant load more than 25,

(k)	an occupant load more than 300 below an open air seating area,

(l)	an interconnected floor space required to conform to Articles 3.2.8.3. to 3.2.8.11,

(m)	a care and treatment occupancy for more than 10 persons receiving care or treatment, or

(n)	a care occupancy for more than 10 persons receiving care.

(3)  If each dwelling unit has direct access to an exterior exit facility leading to ground level, a fire alarm system is not required in an apartment building,

(a)	in which not more than 4 dwelling units share a common means of egress, or

(b)	that is not more than 3 storeys in building height.

(4)  A fire alarm system is not required in a hotel 3 storeys or less in building height provided each suite has direct access to an exterior exit facility leading to ground level.

(5)  A fire alarm system is not required in a storage garage conforming to Article 3.2.2.83. provided there are no other occupancies in the building.

3.2.4.2.  Continuity of Fire Alarm System

(1)  If there are openings through a firewall, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways, the requirements in this Subsection shall apply to the floor areas on both sides of the firewall as if they were in the same building.

(2)  Except as permitted by Sentence (4), if a building contains more than one major occupancy and a fire alarm system is required, a single system shall serve all occupancies.

(3)  Except as permitted by Sentence (4), if a fire alarm system is required in any portion of a building, it shall be installed throughout the building.

(4)  Except as required by Sentence (5), the requirements in this Subsection are permitted to be applied to each portion of a building not more than 3 storeys in building height, in which a vertical fire separation having a fire-resistance rating not less than 1 h separates the portion from the remainder of the building as if it were a separate building, provided there are no openings through the fire separation, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways.

(5)  The permission in Sentence (4) to consider separated portions of a building as separate buildings does not apply to service rooms and storage rooms.

3.2.4.3.  Types of Fire Alarm Systems

(1)  A fire alarm system shall be,

(a)	a single stage system in a Group F, Division 1 occupancy,

(b)	a 2 stage system in a Group B occupancy other than those described in Clause (c),

(c)	a single or 2 stage system in a building 3 storeys or less in building height that contains a Group B, Division 3 occupancy,

(d)	a single stage system in elementary and secondary schools, except for a special needs facility, and

(e)	a single or 2 stage system in all other cases.

3.2.4.4.  Description of Fire Alarm Systems

(1)  A single stage fire alarm system shall, upon the operation of any manual pull station or fire detector, cause an alarm signal to sound on all audible signal devices in the system.

(2)  A 2 stage fire alarm system shall,

(a)	cause an alert signal to sound upon the operation of any manual pull station or fire detector,

(b)	except for a Group B, Division 2 occupancy, automatically cause an alarm signal to sound if the alert signal is not acknowledged within 5 min of its initiation,

(c)	have each manual pull station equipped so that the use of a key or other similar device causes an alarm signal to sound and continue to sound upon the removal of the key or similar device from the manual pull station, and

(d)	in a building containing a hotel,

(i)	cause an alarm signal to sound in the initiating fire zone in the hotel, and

(ii)	cause an alert signal to sound throughout the hotel and such parts of the building as is necessary to alert hotel staff.

(3)  A 2 stage fire alarm system is permitted to be zone coded so that, upon the operation of any manual pull station or fire detector,

(a)	a coded alert signal is sounded indicating the zone of alarm initiation,

(b)	the coded alert signal is repeated in its entirety no fewer than 4 times, and

(c)	a continuous alert signal is sounded upon completion of the coded signals referred to in Clause (b) and Sentence (4).

(4)  If a second manual pull station or fire detector is operated in a fire alarm system with zone coding as permitted by Sentence (3), in a zone other than that for which the first alert signal was sounded, the coded alert signal for the first zone shall be completed before the coded alert signal for the second zone is repeated no fewer than 4 times.

3.2.4.5.  Installation and Verification of Fire Alarm Systems

(1)  Fire alarm systems, including those with voice communication capability, shall be installed in conformance with CAN/ULC-S524, “Installation of Fire Alarm Systems”.

(2)  A fire alarm system shall be verified in conformance with CAN/ULC-S537, “Verification of Fire Alarm Systems”, to ensure satisfactory operation.

3.2.4.6.  Silencing of Alarm Signals

(1)  Except as permitted by Sentence (3), a fire alarm system shall be designed so that when an alarm signal is actuated, it cannot be silenced automatically before a period of time has elapsed that is not less than,

(a)	5 min for a building not required to be equipped with an annunciator, and

(b)	20 min for any other building.

(2)  Except as permitted by Sentences 3.2.4.19.(9), and 3.2.4.22.(2) and (3), a fire alarm system shall not incorporate manual silencing switches other than those installed inside the fire alarm control unit.

(3)  Except as provided in Clause 3.2.4.22.(3)(a), in a care and treatment occupancy an alert signal is permitted to be silenced automatically after 1 min.

3.2.4.7.  Signals to Fire Department

(1)  If a fire alarm system is required to be installed and a single stage system is provided, the system shall be designed to notify the fire department in conformance with Sentence (4) that an alarm signal has been initiated in,

(a)	a Group A occupancy having an occupant load more than 300,

(b)	a Group B occupancy,

(c)	a Group F, Division 1 occupancy,

(d)	a building regulated by the provisions of Subsection 3.2.6., or

(e)	a building containing interconnected floor space required to conform to Articles 3.2.8.3. to 3.2.8.11.

(2)  A fire alarm system that includes waterflow indicating devices shall be designed to notify the fire department, in conformance with Sentence (4), that an alarm has been initiated.

(3)  If a fire alarm system is required to be installed and a 2 stage system is provided, the system shall be designed to notify the fire department, in conformance with Sentence (4), that an alert signal has been initiated.

(4)  Notification of the fire department required by Sentences (1) to (3) shall be by way of,

(a)	signals to a central station conforming to CAN/ULC-S561, “Installation and Services for Fire Signal Receiving Centres and Systems”, or

(b)	the municipal fire alarm system.

(5)  Where a single stage fire alarm system is installed in a building that is not sprinklered, and Sentence (1) does not apply, a legible notice, that is not easily removed, shall be affixed to the wall near each manual pull station stating,

(a)	that the fire department is to be notified in the event of a fire emergency, and

(b)	the emergency telephone number for the municipality or the telephone number of the fire department.

3.2.4.8.  Annunciator and Zone Indication

(1)  Except as permitted in Sentences (3) to (5), an annunciator shall be installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1).

(2)  Except as permitted by Sentence (6), the annunciator required by Sentence (1) shall have separate zone indication of the actuation of the alarm initiating devices in each,

(a)	floor area so that in a building that is not sprinklered, the area of coverage for each zone is neither more than,

(i)	one storey, nor

(ii)	2 000 m2,

(b)	floor area so that in a building that is sprinklered, the area of coverage for each zone is neither more than,

(i)	one storey, nor

(ii)	the system area limits as specified in NFPA 13, “Installation of Sprinkler Systems”,

(c)	shaft required to be equipped with smoke detectors,

(d)	air handling system required to be equipped with smoke detectors,

(e)	contained use area,

(f)	impeded egress zone,

(g)	fire compartment required in Sentence 3.3.3.5.(2), and

(h)	fire compartment required to be separated by vertical fire separations having a fire-resistance rating not less than 2 h, other than dwelling units described in Subsection 3.3.4.

(3)  An annunciator need not be provided for a fire alarm system if not more than one zone indicator is required in Sentence (2).

(4)  If an annunciator is not installed as part of a fire alarm system in conformance with Sentence (1), a visual and audible trouble signal device shall be provided inside the main entrance of the building.

(5)  The requirements in Sentence (1) are waived in a building,

(a)	Reserved

(b)	that has an aggregate area for all storeys of not more than 2 000 m2, and

(c)	that is not more than 3 storeys in building height.

(6)  The area limits of Clause (2)(a) are waived for an interior undivided open space used as an arena, a rink or a swimming pool provided that other spaces in the building that are separated from the open space are individually zoned in accordance with the requirements of Sentence (2).

(7)  A fire alarm control unit installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1), is deemed to satisfy the requirement for an annunciator provided all indicators required for an annunciator or trouble signal device are included on the control unit.

(8)  In a building containing a hotel in which a trouble signal sounding device has a silencing switch, a trouble light shall be installed in,

(a)	the main reception area serving the hotel, or

(b)	another continually-supervised location.

(9)  In a nursing home, a remote audiovisual fire alarm trouble signal shall be located at the main nursing station.

3.2.4.9.  Electrical Supervision

(1)  Electrical supervision shall be provided for a fire alarm system.

(2)  If a fire alarm system is installed in a building, an automatic sprinkler system shall be electrically supervised to indicate a supervisory signal on the building fire alarm system annunciator for each of the following:

(a)	movement of a valve handle that controls the supply of water to sprinklers,

(b)	loss of excess water pressure required to prevent false alarms in a wet pipe system,

(c)	loss of air pressure in a dry pipe system,

(d)	loss of air pressure in a pressure tank,

(e)	a significant change in water level in any water storage container used for fire fighting purposes,

(f)	loss of power to any automatically starting fire pump, and

(g)	a temperature approaching the freezing point in any dry pipe valve enclosure or water storage container used for fire fighting purposes.

3.2.4.10.  Fire Detectors

(1)  Fire detectors required by this Article shall be connected to the fire alarm system.

(2)  Except as provided in Article 3.2.4.15., if a fire alarm system is required, fire detectors shall be installed in,

(a)	storage rooms not within dwelling units,

(b)	service rooms not within dwelling units,

(c)	janitors’ rooms,

(d)	rooms in which hazardous substances are to be used or stored,

(e)	elevator and dumbwaiter shafts,

(f)	a laundry room in a building of residential occupancy, but not one within a dwelling unit, and

(g)	hazardous classrooms and change rooms in elementary and secondary schools.

3.2.4.11.  Smoke and Heat Detectors

(1)  If a fire alarm system is required, smoke detectors shall be installed in,

(a)	each sleeping room and each corridor serving as part of a means of egress from sleeping rooms in portions of a building classified as Group B major occupancy,

(b)	each room in a contained use area and corridors serving those rooms,

(c)	each corridor in portions of a building classified as Group A, Division 1 major occupancy,

(d)	each public corridor in portions of a building classified as Group C major occupancy,

(e)	each exit stair shaft, and

(f)	Reserved

(g)	each corridor serving classrooms in elementary and secondary schools.

(2)  Except as provided in Article 3.2.4.15, if a fire alarm system is required, heat detectors shall be installed in,

(a)	every room in portions of buildings classified as Group A, Division 1,

(b)	except in a hotel, in every suite, and every room not located within a suite, in portions of buildings classified as Group C major occupancy and more than 3 storeys in building height, and

(c)	in a floor area containing a hotel, in every room in a suite and in every room not located in a suite other than washrooms within a suite, saunas, refrigerated areas and swimming pools.

(3)  Smoke detectors required in sleeping rooms of care or detention occupancy shall upon actuation provide an audible and visible signal to staff serving those rooms so that the room or location containing the smoke detector can be easily identified.

3.2.4.12.  Prevention of Smoke Circulation

(1)  If a fire alarm system is installed, an air handling system shall be designed to prevent the circulation of smoke upon a signal from a duct-type smoke detector if the air handling system,

(a)	serves more than one storey,

(b)	serves more than one suite in a storey,

(c)	serves more than one fire compartment required by Sentence 3.3.3.5.(2) or

(d)	is not provided with fire-dampers as permitted by Sentence 3.1.8.8.(8)

3.2.4.13.  Vacuum Cleaning System Shutdown

(1)  A central vacuum cleaning system in a building equipped with a fire alarm system shall be designed to shut down upon actuation of the fire alarm system.

3.2.4.14.  Elevator Emergency Return

(1)  Except as permitted by Sentence (3), in a building having elevators that serve storeys above the first storey and that are equipped with an automatic emergency recall feature, smoke detectors shall be installed in the elevator lobbies on the recall level so that when these smoke detectors are actuated, the elevators will automatically return directly to an alternate floor level.

(2)  Smoke detectors required by Sentence (1) shall be designed as part of the building fire alarm system.

(3)  The alternate floor recall feature required by Sentence (1) is not required if the floor area containing the recall level is sprinklered.

3.2.4.15.  Sprinklers in Lieu of Fire Detectors

(1)  Fire detectors required by Article 3.2.4.10. and heat detectors required by Sentence 3.2.4.11.(2) need not be provided within a floor area if the floor area is sprinklered and the sprinkler system is electrically supervised in conformance with Sentence 3.2.4.9.(2).

3.2.4.16.  System Monitoring

(1)  An automatic sprinkler system shall be equipped with waterflow detecting devices and, if an annunciator is required by Article 3.2.4.8., shall be installed so that each device serves,

(a)	not more than one storey, and

(b)	an area on each storey that is not more than the system area limits as specified in NFPA 13, “Installation of Sprinkler Systems”.

(2)  If a fire alarm system is provided, waterflow indicating devices required by Sentence (1) shall be connected to the fire alarm system so that on actuation an alert signal or an alarm signal is initiated.

3.2.4.17.  Manual Pull Stations

(1)  Except as permitted by Sentences (2) and (3), if a fire alarm system is installed, a manual pull station shall be installed,

(a)	near the principal entrance to the building, and

(b)	near every required exit.

(2)  In a building that is sprinklered, a manual pull station is not required at an exterior egress doorway from a suite that does not lead to an interior shared means of egress in a hotel not more than 3 storeys in building height, provided each suite is served by an exterior exit facility leading directly to ground level.

(3)  In a building that is sprinklered, a manual pull station is not required at an exterior egress doorway from a dwelling unit that does not lead to an interior shared means of egress in a building not more than 3 storeys in building height containing only dwelling units, provided each dwelling unit is served by an exterior exit facility leading directly to ground level.

(4)  In a building referred to in Sentence (2) or (3), manual pull stations shall be installed near doorways leading from shared interior corridors to the exterior.

(5)  In a building containing a hotel, a manual pull station shall be installed in the main reception area serving the hotel.

(6)  Except as permitted by Sentence (3), in Group C apartment buildings, if a pull station is not installed on a floor area in accordance with Sentence (1) or (4),

(a)	a manual pull station shall be installed in every dwelling unit in the floor area near each egress door leading from the dwelling unit,

(b)	smoke detectors shall be installed in the floor area in public corridors and stairwells, and

(c)	fire detectors shall be installed in the floor area in all common public areas and in rooms not located within dwelling units.

(7)  In floor areas where the manual pull stations are located in dwelling units, a legible sign stating FIRE ALARM PULL STATIONS LOCATED IN APARTMENT UNITS shall be posted near every exit in a public corridor.

(8)  Key switch activated pull stations are permitted in an impeded egress zone and a contained use area in Group B, Division 1 and Division 2 occupancies.

3.2.4.18.  Alert and Alarm Signals

(1)  In a 2 stage fire alarm system described in Sentence 3.2.4.4.(2), the same audible signal devices are permitted to be used to sound the alert signals and the alarm signals.

(2)  If audible signal devices with voice reproduction capabilities are intended for paging and similar voice message use, other than during a fire emergency, they shall be installed so that alert signals and alarm signals take priority over all other signals.

(3)  Audible signal devices forming part of a fire alarm or voice communication system shall not be used for playing music or background noise.

(4)  Except as permitted in Sentence (6), visual signal devices shall be installed in addition to audible signal devices,

(a)	in a building or portion of it intended for use primarily by persons with hearing impairment,

(b)	in a public corridor serving a Group A, B, D or E occupancy,

(c)	in a corridor used by the public and in a floor area or part of it where the public may congregate in Group A occupancy, and

(d)	in not less than 10% of the suites of a hotel or motel.

(5)  Visual signal devices are permitted to be installed in lieu of audible signal devices in the compartments referred to in Article 3.3.3.6.

(6)  Visual signal devices required by Clauses (4)(b) and (c) are not required in,

(a)	a classroom, and

(b)	a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants require assistance in evacuation in case of an emergency.

3.2.4.19.  Audibility of Alarm Systems

(1)  Except as permitted in Sentence 3.2.4.18.(5), audible signal devices forming part of a fire alarm system shall be installed in a building so that alert signals and alarm signals are clearly audible throughout the floor area in which they are installed.

(2)  The sound pattern of an alarm signal shall conform to the temporal pattern defined in Clause 4.2 of International Standard ISO 8201, “Acoustics — Audible Emergency Evacuation Signal”.

(3)  The sound patterns of alert signals shall be significantly different from the temporal patterns of alarm signals.

(4)  In all normally occupied spaces, the fire alarm signal sound pressure level,

(a)	shall be not more than 100 dBA when measured at a distance of 3 m from the device, or

(b)	is permitted to be more than 100 dBA provided the sound pressure level measured 2 000 mm above floor level is not more than 100 dBA.

(5)  The sound pressure level in a sleeping room from a fire alarm audible signal device shall be not less than 75 dBA in a building of residential occupancy when any intervening doors between the device and the sleeping room are closed.

(6)  Except as required by Sentence (5), the sound pressure level from a fire alarm audible signal device in a floor area shall be not less than 10 dBA above the ambient noise level, but with a minimum value not less than 65 dBA.

(7)  Fire alarm audible signal devices shall be supplemented by visual signal devices in any floor area in which,

(a)	the ambient noise level is more than 87 dBA, or

(b)	the occupants of the floor area,

(i)	use ear protective devices,

(ii)	are located within an audiometric booth, or

(iii)	are located within sound insulated enclosures.

(8)  Sentence (7) shall also apply in an assembly occupancy in which music and other sounds associated with performances could exceed 100 dBA.

(9)  Except as permitted by Sentence (13), an audible signal device located within a dwelling unit shall incorporate a means that enables the device to be silenced for a period of not more than 10 min, after which the device shall restore to normal operation.

(10)  Audible signal devices within a dwelling unit or a suite of residential occupancy shall be connected to the fire alarm system,

(a)	in a manner such that a single open circuit at one device will not impair the operation of other audible signal devices on the same circuit that serve the other dwelling units or suites of residential occupancy, or

(b)	on separate signal circuits that are not connected to the devices in any other dwelling unit, public corridor, or suites of residential occupancy.

(11)  In a building or part of it classified as a residential occupancy,

(a)	separate circuits shall be provided for audible signal devices on each floor area, and

(b)	audible signal devices within dwelling units or suites of residential occupancy shall be wired on separate signal circuits from those not within suites of residential occupancy or dwelling units.

(12)  Audible signal devices shall be installed in a service space referred to in Sentence 3.2.1.1.(9) and shall be connected to the fire alarm system.

(13)  Audible signal devices, within dwelling units that are wired on separate signal circuits, need not include a means for silencing as required by Sentence (9) provided the fire alarm system includes a provision for the automatic signal silence within dwelling units, where,

(a)	the automatic signal silence cannot occur within the first 60 s of operation or within the zone of initiation,

(b)	a subsequent alarm elsewhere in the building will reactuate the silenced audible signal devices within dwelling units,

(c)	after a period of not more than 10 min, the silenced audible signal devices will be restored to continuous audible signal if the alarm is not acknowledged, and

(d)	the voice communication system referred to in Article 3.2.4.22. has a provision to override the automatic signal to allow the transmission of voice messages through silenced audible signal device circuits that serve the dwelling units.

(14)  If a 2 stage fire alarm system has been installed with an automatic signal silence as described in Sentence (13), the system shall be designed so that any silenced audible signal devices serving dwelling units are reactuated whenever an alarm signal is required to be transmitted as part of the second stage.

3.2.4.20.  Visual Signals

(1)  Visual signal devices required by Sentences 3.2.4.18.(4) and 3.2.4.19.(7) and (8) shall be installed so that the signal from at least one device is visible throughout the floor area or portion of it in which they are installed.

(2)  Visual signal devices permitted by Sentence 3.2.4.18.(5) shall be installed so that the signal from at least one device is visible throughout the compartment in which they are installed.

3.2.4.21.  Smoke Alarms

(1)  Smoke alarms conforming to CAN/ULC-S531, “Smoke Alarms”, shall be installed in each dwelling unit and, except for care or detention occupancies required to have a fire alarm system, in each sleeping room not within a dwelling unit.

(2)  At least one smoke alarm shall be installed on each storey and mezzanine of a dwelling unit.

(3)  On any storey of a dwelling unit containing sleeping rooms, a smoke alarm shall be installed in a location between the sleeping rooms and the remainder of the storey, and if the sleeping rooms are served by a hallway, the smoke alarm shall be located in the hallway.

(4)  A smoke alarm shall be installed on or near the ceiling.

(5)  A smoke alarm shall be installed with permanent connections to an electrical circuit and shall have no disconnect switches between the overcurrent device and the smoke alarm.

(6)  If more than one smoke alarm is required in a dwelling unit, the smoke alarms shall be wired so that the actuation of one smoke alarm will cause all smoke alarms within the dwelling unit to sound.

(7)  A smoke alarm required by Sentence (1) shall be installed in conformance with CAN/ULC-S553, “Installation of Smoke Alarms”.

(8)  A manually operated device is permitted to be incorporated within the circuitry of a smoke alarm installed in a dwelling unit so that it will silence the signal emitted by the smoke alarm for a period of not more than 10 min, after which the smoke alarm will reset and again sound the alarm if the level of smoke in the vicinity is sufficient to reactuate the smoke alarm.

(9)  The sound patterns of smoke alarms shall be significantly different from the temporal patterns of alarm signals.

3.2.4.22.  Voice Communication Systems

(1)  A voice communication system required by Subsection 3.2.6. or Clause 3.3.2.4.(14)(f) shall consist of,

(a)	a 2-way communication system in each floor area, with connections to the central alarm and control facility and to the mechanical control centre, and

(b)	loudspeakers operated from the central alarm and control facility that are designed and located so as to be audible and the messages intelligible in all parts of the building, except that this requirement does not apply to elevator cars.

(2)  The voice communication system referred to in Sentence (1) shall include a means to silence the alarm signal in a single stage fire alarm system while voice messages are being transmitted, but only after the alarm signal has initially sounded for not less than 30 s.

(3)  The voice communication system referred to in Sentence (1) shall include a means to silence the alert signal and the alarm signal in a 2 stage fire alarm system while voice messages are being transmitted, but only after the alert signal has initially sounded for not less than,

(a)	10 s in hospitals that have supervisory personnel on duty for twenty-four hours each day, or

(b)	30 s for all other occupancies.

(4)  The voice communication system referred to in Clause (1)(b) shall be designed so that the alarm signal can be selectively transmitted to any zone or zones while maintaining an alert signal or selectively transmitting voice messages to any other zone or zones in the building.

(5)  The 2-way communication system referred to in Clause (1)(a) shall be installed so that emergency telephones are located in each floor area near exit stair shafts.

3.2.5.  Provisions for Fire Fighting

3.2.5.1.  Access to Above Grade Storeys

(1)  Except for storeys below the first storey, direct access for fire fighting shall be provided from the outdoors to every storey that is not sprinklered and whose floor level is less than 25 m above grade, by at least one unobstructed window or access panel for each 15 m of wall in each wall required to face a street by Subsection 3.2.2.

(2)  An opening for access required by Sentence (1) shall,

(a)	have a sill no higher than 1070 mm above the inside floor, and

(b)	be not less than 1 100 mm high by not less than,

(i)	550 mm wide for a building not designed for the storage or use of dangerous goods, or

(ii)	750 mm wide for a building designed for the storage or use of dangerous goods.

(3)  Access panels above the first storey shall be readily openable from both inside and outside, or the opening shall be glazed with plain glass.

3.2.5.2.  Access to Basements

(1)  Direct access from at least one street shall be provided from the outdoors to each basement,

(a)	that is not sprinklered, and

(b)	that has horizontal dimension more than 25 m.

(2)  The access required by Sentence (1) is permitted to be provided by,

(a)	doors, windows or other means that provide an opening not less than 1 100 mm high and 550 mm wide, with a sill no higher than 900 mm above the inside floor, or

(b)	an interior stairway immediately accessible from the outdoors.

3.2.5.3.  Roof Access

(1)  On a building more than 3 storeys in building height where the slope of the roof is less than 1 in 4, all main roof areas shall be provided with direct access from the floor areas immediately below, either by,

(a)	a stairway, or

(b)	a hatch not less than 550 mm by 900 mm with a fixed ladder.

(2)  Clearance and access around roof signs or other obstructions shall provide,

(a)	a passage not less than 900 mm wide by 1 800 mm high, clear of all obstructions except for necessary horizontal supports not more than 600 mm above the roof surface,

(i)	around every roof sign, and

(ii)	through every roof sign at locations not more than 15 m apart, and

(b)	a clearance of not less than 1 200 mm between any portion of a roof sign and any opening in the exterior wall face or roof of the building in which it is erected.

3.2.5.4.  Access Routes

(1)  A building that is more than 3 storeys in building height or more than 600 m2 in building area shall be provided with access routes for fire department vehicles,

(a)	to the building face having a principal entrance, and

(b)	to each building face having access openings for fire fighting as required by Articles 3.2.5.1. and 3.2.5.2.

3.2.5.5.  Location of Access Routes

(1)  Access routes required by Article 3.2.5.4. shall be located so that the principal entrance and every access opening required by Articles 3.2.5.1. and 3.2.5.2. are located not less than 3 m and not more than 15 m from the closest portion of the access route required for fire department use, measured horizontally from the face of the building.

(2)  Access routes shall be provided to a building so that,

(a)	for a building provided with a fire department connection, a fire department pumper vehicle can be located adjacent to the hydrants referred to in Article 3.2.5.16.,

(b)	for a building not provided with a fire department connection, a fire department pumper vehicle can be located so that the length of the access route from a hydrant to the vehicle plus the unobstructed path of travel for the fire fighter from the vehicle to the building is not more than 90 m, and

(c)	the unobstructed path of travel for the fire fighter from the vehicle to the building is not more than 45 m.

(3)  The unobstructed path of travel for the fire fighter required by Sentence (2) from the vehicle to the building shall be measured from the vehicle to the fire department connection provided for the building, except that if no fire department connection is provided, the path of travel shall be measured to the principal entrance of the building.

(4)  If a portion of a building is completely cut off from the remainder of the building so that there is no access to the remainder of the building, the access routes required by Sentence (2) shall be located so that the unobstructed path of travel from the vehicle to one entrance of each portion of the building is not more than 45 m.

3.2.5.6.  Access Route Design

(1)  A portion of a roadway or yard provided as a required access route for fire department use shall,

(a)	have a clear width not less than 6 m, unless it can be shown that lesser widths are satisfactory,

(b)	have a centreline radius not less than 12 m,

(c)	have an overhead clearance not less than 5 m,

(d)	have a change of gradient not more than 1 in 12.5 over a minimum distance of 15 m,

(e)	be designed to support the expected loads imposed by fire fighting equipment and be surfaced with concrete, asphalt or other material designed to permit accessibility under all climatic conditions,

(f)	have turnaround facilities for any dead-end portion of the access route more than 90 m long, and

(g)	be connected with a public thoroughfare.

3.2.5.7.  Water Supply

(1)  An adequate water supply for fire fighting shall be provided for every building.

(2)  Hydrants shall be located within 90 m horizontally of any portion of a building perimeter that is required to face a street in Subsection 3.2.2.

3.2.5.8.  Reserved

3.2.5.9.  Reserved

3.2.5.10.  Reserved

3.2.5.11.  Reserved

3.2.5.12.  Reserved

3.2.5.13.  Automatic Sprinkler Systems

(1)  Except as permitted by Sentences (2) to (4), an automatic sprinkler system shall be designed, constructed, installed and tested in conformance with NFPA 13, “Installation of Sprinkler Systems”.

(2)  Instead of the requirements of Sentence (1), NFPA 13R, “Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Stories in Height”, is permitted to be used for the design, construction, installation and testing of an automatic sprinkler system installed in a building,

(a)	of residential occupancy that is not more than 4 storeys in building height or

(b)	of Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants require assistance in evacuation in case of an emergency.

(3)  Instead of the requirements of Sentence (1), NFPA 13D, “Installation of Sprinkler Systems in One- and Two-Family Dwellings and Mobile Homes”, is permitted to be used for the design, construction, installation and testing of an automatic sprinkler system installed in a building of residential occupancy that contains not more than 2 dwelling units.

(4)  If a building contains fewer than 9 sprinklers, the water supply for these sprinklers is permitted to be supplied from the domestic water system for the building provided the required flow for the sprinklers can be met by the domestic system.

(5)  If a water supply serves both an automatic sprinkler system and a system serving other equipment, control valves shall be provided so that either system can be shut off independently.

(6)  Notwithstanding the requirements of the standards referenced in Sentences (1) and (2) for the installation of automatic sprinkler systems, sprinklers shall not be omitted in any room or closet in the storey immediately below a roof assembly if the fire-resistance rating of the roof assembly is waived as permitted by Article 3.2.2.17.

(7)  Fast response sprinklers shall be installed in care or detention occupancies and in sprinklered residential occupancies.

(8)  Sprinklers in elevator machine rooms shall have a temperature rating not less than that required for an intermediate temperature classification and shall be protected against physical damage.

3.2.5.14.  Combustible Sprinkler Piping

(1)  Combustible sprinkler piping shall be used only for wet systems in residential occupancies and other light hazard occupancies.

(2)  Combustible sprinkler piping shall meet the requirements of ULC/ORD-199P-M, “Combustible Piping for Sprinkler Systems”.

(3)  Except as permitted by Sentence (5), combustible sprinkler piping shall be separated from the area served by the sprinkler system, and from any other fire compartment, by ceilings, walls, or soffits consisting of, as a minimum,

(a)	lath and plaster,

(b)	gypsum board not less than 9.5 mm thick,

(c)	plywood not less than 13 mm thick, or

(d)	a suspended membrane ceiling with,

(i)	steel suspension grids, and

(ii)	lay-in panels or tiles having a mass not less than 1.7 kg/m2.

(4)  Except as permitted by Sentence (5), combustible sprinkler piping may be located above a ceiling, provided that the distance between the edge of any ceiling opening that is not protected in conformance with Sentence (3) and the nearest sprinkler is not more than 300 mm.

(5)  The protection required by Sentences (3) and (4) is permitted to be waived where combustible sprinkler piping has been tested in conformance with ULC/ORD-C199P-M, “Combustible Piping for Sprinkler Systems”, and has been shown to meet the requirements in that document without additional protection.

3.2.5.15.  Sprinklered Service Space

(1)  An automatic sprinkler system shall be installed in a service space referred to in Sentence 3.2.1.1.(9) if flooring for access within the service space is other than catwalks.

(2)  The sprinkler system required by Sentence (1) shall be equipped with waterflow detecting devices, with each device serving not more than one storey.

(3)  The waterflow detecting devices required by Sentence (2) shall be connected to the fire alarm system, to

(a)	initiate an alert signal in a 2 stage system or an alarm signal in a single stage system, and

(b)	indicate separately on the fire alarm system annunciator the actuation of each device.

(4)  If a building is sprinklered, sprinkler protection need not be provided in the space below a raised floor in a computer room,

(a)	if the optical fibre cables and electrical wires and cables in this space conform to the test requirements in Article 3.1.5.21.,

(b)	if the building is of noncombustible construction and other combustible components are limited to those permitted in Subsection 3.1.5.,

(c)	if this space is used to circulate conditioned air and the air handling system is designed to prevent the circulation of smoke upon a signal from a smoke detector,

(d)	if all of this space is easily accessible by providing access sections or panels in the raised floor, and

(e)	if the computer room is more than 2 000 m2 and the annunciator has separate zone indicators of the actuation of smoke detectors located in this space so that the coverage for each zone is not more than 2 000 m2.

(5)  Where a room, chute or bin is required to be sprinklered as indicated in Sentence 3.3.4.3.(1), Article 3.6.2.5. and Sentence 3.6.3.3.(6), the sprinklers may be supplied with water from the fire standpipe system provided that,

(a)	except for a chute, not more than 8 sprinkler heads are required to protect any room or bin based on a maximum coverage of 12 m2 per sprinkler head,

(b)	the standpipe riser is,

(i)	not less than 6 in. in diameter, or

(ii)	hydraulically designed to meet combined water supply as specified in Clause (c),

(c)	the water supply for a standpipe system, pumping capability and water storage facility, if required, is increased to supply 95 L/min for each sprinkler head over and above the requirements for the standpipe system up to maximum 760 L/min for sprinklers,

(d)	a waterflow detecting device shall be installed in the sprinkler main adjacent to the point of connection to the standpipe riser, and

(e)	the activation of each waterflow detecting device in Clause (d) shall be indicated separately on the fire alarm system annunciator.

3.2.5.16.  Fire Department Connections

(1)  The fire department connection for a standpipe system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed.

(2)  The fire department connection for an automatic sprinkler system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed.

(3)  The fire department connections required in Sentences (1) and (2) shall be,

(a)	located on the outside of a building adjacent to a street or an access route, not less than 300 mm and not more than 900 mm above ground level, and

(b)	provided with two 65 mm hose connections with female swivel hose couplings.

3.2.5.17.  Portable Fire Extinguishers

(1)  Portable fire extinguishers shall be installed in all buildings, except within dwelling units, in conformance with the provisions of Part 6 of the Fire Code made under the Fire Protection and Prevention Act, 1997.

(2)  In a Group B, Division 1 major occupancy, portable fire extinguishers are permitted to be located in secure areas, or in lockable cabinets provided,

(a)	identical keys for all cabinets are located at all supervisory or security stations, or

(b)	electrical remote release devices are provided and are connected to an emergency power supply.

3.2.5.18.  Protection from Freezing

(1)  Equipment forming part of a fire protection system shall be protected from freezing if,

(a)	it could be adversely affected by freezing temperatures, and

(b)	it is located in an unheated area.

3.2.5.19.  Fire Pumps

(1)  A fire pump having a rated net head pressure greater than 280 kPa shall be installed in accordance with the requirements of NFPA 20, “Installation of Stationary Pumps for Fire Protection”.

3.2.6.  Additional Requirements for High Buildings

3.2.6.1.  Application

(1)  This Subsection applies to a building,

(a)	of Group A, D, E or F major occupancy classification that is more than,

(i)	36 m high, measured between grade and the floor level of the top storey, or

(ii)	18 m high, measured between grade and the floor level of the top storey, and in which the cumulative or total occupant load on or above any storey above grade, other than the first storey, divided by 1.8 times the width in metres of all exit stairs at that storey, exceeds 300,

(b)	containing a Group B major occupancy in which the floor level of the highest storey of that major occupancy is more than 18 m above grade,

(c)	containing a floor area or part of a floor area located above the third storey designed or intended as a Group B, Division 2 or 3 occupancy, and

(d)	containing a Group C major occupancy whose floor level is more than 18 m above grade.

3.2.6.2.  Limits to Smoke Movement

(1)  Except as permitted in Sentence 3.2.6.6.(2), a building to which this Subsection applies shall be designed in accordance with Sentences (2) to (4) and Articles 3.2.6.3. to 3.2.6.7. to limit the danger to occupants and fire fighters from exposure to smoke in a building fire.

(2)  Except as provided in Articles 3.2.6.4. to 3.2.6.6., a building referred to in Sentence (1), shall be designed so that, during a period of 2 h after the start of a fire, all floor areas that are above the lowest exit storey will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Supplementary Standard SB-1.

(3)  Except as provided in Articles 3.2.6.4 and 3.2.6.6., a building referred to in Sentence (1), shall be designed so that during a period of 2 h after the start of a fire, the limit described in Sentence (2) on the movement of contaminated air into other floor areas is not exceeded in,

(a)	each exit stair serving storeys above the lowest exit level, and

(b)	each exit stair serving storeys below the lowest exit level.

(4)  Except as provided in Articles 3.2.6.4. and 3.2.6.6., a building referred to in Sentence (1), shall be designed so that during a period of 2 h after the start of a fire, the limit described in Sentence (2) on the movement of contaminated air into other floor areas is not exceeded in a shaft that contains an elevator for use by fire fighters required by Article 3.2.6.9.

3.2.6.3.  Areas of Refuge

(1)  In a building of Group C major occupancy classification, the requirements of Sentence 3.2.6.2.(2) are waived in buildings where occupants above the first storey can enter and be safely accommodated in floor areas or parts of floor areas that are designated as areas of refuge on the plans and are identified as such in the building.

(2)  Except as required in Sentence (3), the areas of refuge referred to in Sentence (1) shall be located on every fifth storey.

(3)  The areas of refuge referred to in Sentence (1) shall be located on every storey if the building is more than 75 m high, measured between grade and the floor level of the top storey.

(4)  The areas of refuge referred to in Sentence (1) shall,

(a)	provide not less than 0.5 m2 of floor space per ambulatory occupant and 1.5 m2 of floor space per non-ambulatory occupant,

(b)	have access corridors and doors leading to each designated part of a floor area on the same storey sufficient to provide 3.67 mm of width for every person who may have to use these passages to reach the designated part of a floor area,

(c)	have access stairs from intervening storeys leading to each designated part of a floor area sufficient to provide 5.5 mm of width for every person who may have to use these stairs to reach the designated part of a floor area, and

(d)	not contain more than 1% by volume of contaminated air from the fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Supplementary Standard SB-1.

3.2.6.4.  Sprinklered Buildings

(1)  The requirements of Sentences 3.2.6.2.(2) and (4), and Clause 3.2.6.2.(3)(a) are waived when a building is sprinklered and,

(a)	the sprinkler system is equipped with a water flow and supervisory signal system that will,

(i)	transmit automatically a waterflow signal directly to the fire department, or through an independent central station,

(ii)	transmit automatically other supervisory signals to a proprietary control centre or to an independent central station, and

(iii)	actuate a signal at the central alarm and control facility described in Article 3.2.6.12.,

(b)	each stairway that serves storeys above the lowest exit level is vented to the outdoors at or near the bottom of the stair shaft,

(c)	measures are taken to limit movement of smoke from a fire in a floor area below the lowest exit storey into upper storeys, and

(d)	except for exhaust fans in kitchens, washrooms and bathrooms in dwelling units, and except for fans used for smoke venting in Article 3.2.6.10., air moving fans in a system that serves more than 2 storeys shall be designed and installed so that in the event of a fire these fans can be stopped by means of a manually operated switch at the central alarm and control facility.

3.2.6.5.  Exception for Lower Buildings

(1)  The requirements of Sentence 3.2.6.2.(2) are waived in a building of Group C major occupancy classification where,

(a)	the building is not more than 75 m high measured between grade and the floor level of the top storey, and

(b)	the number of occupants of storeys above grade is not more than 3.6 times the area in square metres of treads and landings in the exit stairs serving these storeys.

3.2.6.6.  Residential Buildings

(1)  The requirements of Sentences 3.2.6.2.(2) and (4) and Clause 3.2.6.2.(3)(a) are waived in a building of Group C major occupancy classification,

(a)	where each suite above grade has direct access to an exterior balcony that conforms to the requirements of Sentence 3.3.1.7.(7),

(b)	where each stairway that serves storeys above the lowest exit level is vented to the outdoors at or near the bottom of the stair shaft,

(c)	where measures are taken to limit movement of smoke from a fire in a floor area below the lowest exit storey into upper storeys, and

(d)	where, except for exhaust fans in kitchens, washrooms and bathrooms in dwelling units, air moving fans are designed and installed so that in the event of a fire such fans can be stopped by means of a manually operated switch at the central alarm and control facility where the system serves more than 2 storeys.

(2)  The requirements of Sentences 3.2.6.2.(2) and (3) are waived in a Group C major occupancy apartment building.

3.2.6.7.  Connected Buildings

(1)  If a building described in Sentence 3.2.6.1.(1) is connected to any other building, measures shall be taken to limit movement of contaminated air from one building into another during a fire.

3.2.6.8.  Emergency Operation of Elevators

(1)  Manual emergency recall shall be provided for all elevators serving storeys above the first storey.

(2)  Key-operated switches for emergency recall described by Sentence (1) shall be provided in a conspicuous location at,

(a)	each elevator lobby on the recall level, and

(b)	the central alarm and control facility required in Article 3.2.6.12.

(3)  In-car emergency service switches shall be provided in all elevator cars.

(4)  Keys to operate the switches required by Sentences (2) and (3) shall be,

(a)	provided in a suitably identified box conspicuously located on the outside of an elevator hoistway near the central alarm and control facility required by Article 3.2.6.12., and

(b)	at the central alarm and control facility.

(5)  Automatic emergency recall operation shall be provided for all elevators serving storeys above the first storey in unsprinklered buildings.

(6)  The automatic emergency recall feature in Sentence (5) shall be actuated by,

(a)	smoke detectors installed in each elevator lobby on each storey, or

(b)	the building fire alarm system.

(7)  Smoke detectors in Sentence (6) shall be designed as part of the building fire alarm system.

3.2.6.9.  Elevator for Use by Fire Fighters

(1)  At least one elevator shall be provided for use by fire fighters in conformance with Sentences (2) to (6).

(2)  The elevator referred to in Sentence (1) shall have a usable platform area not less than 2.2 m2 and shall be capable of carrying a load of 900 kg to the top floor that it serves from a landing on the storey containing the entrance for fire fighter access referred to in Articles 3.2.5.4. and 3.2.5.5. within 1 min.

(3)  Except when Measure K of Supplementary Standard SB-4 is used, each elevator for use by fire fighters shall,

(a)	be provided with a closure at each shaft opening so that the interlock mechanism remains mechanically engaged and electrical continuity is maintained in the interlock circuits and associated wiring is operational for a period of not less than 1 h when the assembly is subjected to the standard fire exposure described in CAN4-S104-M, “Fire Tests of Door Assemblies”,

(b)	be protected with a vestibule containing no occupancy and separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min, or

(c)	be protected with a corridor containing no occupancy and separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(4)  Except as permitted in Sentence (5), an elevator referred to in Sentence (1) shall be capable of providing transportation from the storey containing the entrance for fire fighter access referred to in Articles 3.2.5.4. and 3.2.5.5. to every floor that is above grade in the building and that is normally served by the elevator system.

(5)  If it is necessary to change elevators to reach any floor referred to in Sentence (4), the system shall be designed so that not more than one change of elevator is required when travelling to any floor in the building from the storey containing the entrance for fire fighter access referred to in Articles 3.2.5.4. and 3.2.5.5.

(6)  Electrical conductors for the operation of the elevator referred to in Sentence (1) shall be,

(a)	installed in service spaces conforming to Section 3.6. that do not contain other combustible material, or

(b)	protected against exposure to fire from the service entrance of the emergency power supply, or the normal service entrance of the normal power supply, to the equipment served, to ensure operation for a period of 1 h when subjected to the standard fire exposure described in CAN4-S101-M, “Fire Endurance Tests of Building Construction and Materials”.

3.2.6.10.  Venting to Aid Fire Fighting

(1)  Means of venting each floor area to the outdoors shall be provided by windows, wall panels or smoke shafts, except that in a sprinklered floor area, the floor area is permitted to be vented by the building exhaust system.

(2)  Venting described in Sentence (1) shall conform to the requirements in Supplementary Standard SB-4.

(3)  Fixed glass windows shall not be used for the venting required by Sentence (1) if the breaking of the windows could endanger pedestrians below.

(4)  Openable windows used for the venting required by Sentence (1) shall be permanently marked so that they are easily identifiable.

(5)  Elevator hoistways shall not be designed for the venting required by Sentence (1).

3.2.6.11.  Reserved

3.2.6.12.  Central Alarm and Control Facility

(1)  A central alarm and control facility shall be provided on the storey containing the entrance for fire fighter access referred to in Articles 3.2.5.4. and 3.2.5.5. in a location that,

(a)	is readily accessible to fire fighters entering the building, and

(b)	takes into account the effect of background noise likely to occur under fire emergency conditions, so that the facility can properly perform its required function under such conditions.

(2)  The central alarm and control facility required in Sentence (1) shall include,

(a)	means to control the voice communication system required by Article 3.2.6.13., so that messages can be sent to,

(i)	all loudspeakers simultaneously

(ii)	to individual floor areas, and

(iii)	exit stairwells,

(b)	means to indicate audibly and visually alert signals and alarm signals and a switch to,

(i)	silence the audible portion of these signals, and

(ii)	indicate visually that the audible portion has been silenced,

(c)	means to indicate visually that elevators are on emergency recall,

(d)	an annunciator conforming to Article 3.2.4.8.,

(e)	means to transmit alert signals and alarm signals to the fire department in conformance with Article 3.2.4.7.,

(f)	means to release hold-open devices on doors to vestibules,

(g)	means to manually actuate alarm signals in the building selectively to any zone or zones,

(h)	means to silence the alarm signals referred to in Clause (g) in conformance with Sentences 3.2.4.22.(2) and (3),

(i)	means, as appropriate to the measure for fire safety provided in the building, to,

(i)	actuate auxiliary equipment, or

(ii)	communicate with a continually staffed auxiliary equipment control centre,

(j)	means to communicate with telephones in elevator cars, separate from connections to fire fighters’ telephones, if elevator cars are required by the Elevating Devices Act to be equipped with a telephone,

(k)	means to indicate visually, individual sprinkler system waterflow signals,

(l)	means to indicate audibly and visually, sprinkler system supervisory signals,

(m)	a switch to silence the audible portion of a supervisory signal, and

(n)	visual indication that the audible portion of a supervisory signal has been silenced.

3.2.6.13.  Voice Communication System

(1)  A voice communication system or systems conforming to Article 3.2.4.22. shall be provided in a building if,

(a)	the floor of the top storey, is more than 36 m above grade, or

(b)	a floor area or part of a floor area located above the third storey is designed or intended for use as a Group B, Division 2 or 3 occupancy.

3.2.6.14.  Testing

(1)  The systems for control of smoke movement and mechanical venting required by Articles 3.2.6.2. and 3.2.6.10. shall be tested to ensure satisfactory operation in accordance with the procedures described in Supplementary Standard B-4.

3.2.7.  Lighting and Emergency Power Systems

3.2.7.1.  Minimum Lighting Requirements

(1)  An exit, a public corridor, a corridor providing access to exit for the public, a corridor serving patients or residents in a Group B, Division 2 or Division 3 occupancy, a corridor serving classrooms, an electrical equipment room, a transformer vault and a hoistway pit shall be equipped to provide illumination to an average level not less than 50 lx at floor or tread level and at angles and intersections at changes of level where there are stairs or ramps.

(2)  Rooms and spaces used by the public shall be illuminated as described in Article 9.34.2.7.

(3)  Lighting outlets in a building of residential occupancy shall be provided in conformance with Subsection 9.34.2.

(4)  Elevator machine rooms shall be equipped to provide illumination to an average level of not less than 100 lx at floor level.

(5)  Every place of assembly intended for the viewing of motion pictures or the performing arts, shall be equipped to provide an average level of illumination at floor level in the aisles of not less than 2 lx during the viewing.

(6)  Every area where food is intended to be processed, prepared or manufactured and where equipment or utensils are intended to be cleaned shall be equipped to provide illumination to a level of not less than 500 lx measured at the floor level.

(7)  Every storage room, dressing room, sanitary facility, service area and corridor serving the areas in Sentence (6) shall be equipped to provide illumination to a level of not less than 300 lx measured at the floor level.

3.2.7.2.  Recessed Lighting Fixtures

(1)  A recessed lighting fixture shall not be located in an insulated ceiling unless the fixture is designed for this type of installation.

3.2.7.3.  Emergency Lighting

(1)  Emergency lighting shall be provided to an average level of illumination not less than 10 lx at floor or tread level in,

(a)	exits,

(b)	principal routes providing access to exit in an open floor area and in service rooms,

(c)	corridors used by the public,

(d)	corridors serving patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy,

(e)	corridors serving classrooms,

(f)	underground walkways,

(g)	public corridors,

(h)	floor areas or parts of them where the public may congregate in,

(i)	Group A, Division 1 occupancies, or

(ii)	Group A, Division 2 and 3 occupancies having an occupant load of 60 or more,

(i)	floor areas or parts of them in day care centres where persons are cared for,

(j)	food preparation areas in commercial kitchens,

(k)	principal routes providing access to exit in a floor area that is not subdivided into rooms or suites of rooms served by corridors in a business and personal services occupancy, a mercantile occupancy or an industrial occupancy, and

(l)	internal corridors or aisles serving as principal routes to exits in a business and personal services occupancy, a mercantile occupancy or an industrial occupancy that is subdivided into rooms or suites of rooms, and is not served by a public corridor.

(2)  Emergency lighting to provide an average level of illumination of not less than 10 lx at floor or catwalk level shall be included,

(a)	in a service space referred to in Sentence 3.2.1.1.(9), and

(b)	on a shelf and rack storage system referred to in Sentence 3.16.1.4.(2).

(3)  The minimum value of the illumination required by Sentences (1) and (2) shall be not less than 1 lx.

(4)  In addition to the requirements of Sentences (1) to (3), the installation of battery-operated emergency lighting in health care facilities shall conform to the appropriate requirements of CSA Z32, “Electrical Safety and Essential Electrical Systems in Health Care Facilities”.

3.2.7.4.  Emergency Power for Lighting

(1)  An emergency power supply shall be,

(a)	provided to maintain the emergency lighting required by this Subsection from a power source such as batteries or generators that will continue to supply power in the event that the regular power supply to the building is interrupted, and

(b)	so designed and installed that upon failure of the regular power it will assume the electrical load automatically for a period of,

(i)	2 h for a building within the scope of Subsection 3.2.6.,

(ii)	1 h for a building of Group B major occupancy classification that is not within the scope of Subsection 3.2.6., and

(iii)	30 min for a building of any other occupancy.

(2)  If self-contained emergency lighting units are used, they shall conform to CSA C22.2 No. 141, “Unit Equipment for Emergency Lighting”.

3.2.7.5.  Emergency Power Supply Installation

(1)  Except as required by Articles 3.2.7.6. and 3.2.7.7., an emergency electrical power system shall be installed in conformance with CSA C282, “Emergency Electrical Power Supply for Buildings”.

3.2.7.6.  Emergency Power for Hospitals

(1)  Except as required by Article 3.2.7.7., an emergency electrical power system for emergency equipment required by this Part for health care facilities shall be installed in conformance with CSA Z32, “Electrical Safety and Essential Electrical Systems in Health Care Facilities”.

3.2.7.7.  Fuel Supply Shut-off Valves and Exhaust Pipes

(1)  If a liquid or gas fuel-fired engine or turbine for an emergency electric power supply is dependent on a fuel supply from outside the building, the fuel supply shall be provided with a suitably-identified separate shut-off valve outside the building.

(2)  Where pipes for exhaust gases from emergency power systems penetrate required fire separations, they shall be enclosed in a separate service space having a fire-resistance rating equal to that of the penetrated floor assembly, but not less than 45 min.

3.2.7.8.  Emergency Power for Fire Alarm Systems

(1)  Fire alarm systems, including those incorporating a voice communication system, shall be provided with an emergency power supply conforming to Sentences (2) to (4).

(2)  The emergency power supply required by Sentence (1) shall be supplied from,

(a)	a generator,

(b)	batteries, or

(c)	a combination of the items described in Clauses (a) and (b).

(3)  The emergency power supply required by Sentence (1) shall be capable of providing,

(a)	supervisory power for not less than 24 h, and

(b)	immediately following, emergency power under full load for not less than,

(i)	2 h for a building within the scope of Subsection 3.2.6.,

(ii)	1 h for a building classified as Group B major occupancy that is not within the scope of Subsection 3.2.6.,

(iii)	5 min for a building not required to be equipped with an annunciator, and

(iv)	30 min for any other building.

(4)  The emergency power supply required by Sentence (1) shall be designed so that, in the event of a failure of the normal power source, there is an immediate automatic transfer to emergency power with no loss of information.

3.2.7.9.  Emergency Power for Building Services

(1)  An emergency power supply capable of operating under a full load for not less than 2 h shall be provided by an emergency generator for,

(a)	every elevator serving storeys above the first storey in a building that is more than 36 m high measured between grade and the floor level of the top storey and every elevator for fire fighters in conformance with Sentence (2),

(b)	water supply for fire fighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, and the building is within the scope of Subsection 3.2.6.,

(c)	fans and other electrical equipment that are installed to maintain the air quality specified in Article 3.2.6.2., and

(d)	fans required for venting by Article 3.2.6.10.

(2)  Except as permitted by Sentence (3), the emergency power supply for elevators required by Clause (1)(a) shall be capable of operating all elevators for fire fighters plus one additional elevator simultaneously.

(3)  Sentence (2) does not apply if the time to recall all elevators under emergency power supply is not more than 5 min, each from its most remote storey to,

(a)	the storey containing the entrance for fire fighter access referred to in Articles 3.2.5.4 and 3.2.5.5., or

(b)	to a transfer lobby.

(4)  Except as provided by Sentence (5), an emergency power supply capable of operating under a full load for not less than 30 min shall be provided by emergency generator for water supply for fire fighting in conformance with Article 3.2.5.7., if the supply is dependent on electrical power supplied to the building, and the building is not within the scope of Subsection 3.2.6.

(5)  Sentence (4) does not apply to the water supply for a standpipe system.

3.2.7.10.  Protection of Electrical Conductors

(1)  Electrical conductors that are used in conjunction with fire alarm systems and with emergency equipment described in Articles 3.2.6.2. to 3.2.6.8., and Sentences 3.3.3.6.(1) and 3.3.3.7.(4) shall conform to Sentences (2) to (8).

(2)  Except as permitted by Sentences (6) to (8), electrical conductors referred to in Sentence (1) shall conform to ULC-S139, “Fire Test for Evaluation of Integrity of Electrical Cables”, including hose stream application, to provide a circuit integrity rating of not less than 1 h.

(3)  The electrical conductors referred to in Sentence (2) are those that extend from the source of emergency power to,

(a)	the equipment served, or

(b)	the distribution equipment supplying power to the equipment served if both are in the same room.

(4)  If a fire alarm transponder or annunciator is connected to, but located in, a different fire compartment than the central processing unit or another transponder, all wiring between the transponder or annunciator and the central processing unit or other transponder shall be protected against exposure to fire in accordance with Sentence (2).

(5)  If a panelboard supplies power to emergency lighting, the power supply conductors to the panelboard shall be protected against exposure to fire in accordance with Sentence (2).

(6)  Electrical conductors located in a service space that contains no other combustible material and is separated from the remainder of the building by a fire separation that has a fire-resistance rating not less than 1 h need not conform to Sentence (2).

(7)  Fire alarm system branch circuits within a storey that connect transponders and individual devices need not conform to Sentence (2).

(8)  Wiring from a panelboard referred to in Sentence (5) to emergency lighting units in the same storey need not conform to Sentence (2).

3.2.8.  Mezzanines and Openings through Floor Assemblies

3.2.8.1.  Application

(1)  Except as permitted by Article 3.2.8.2. and Sentence 3.3.4.2.(3), the portions of a floor area or a mezzanine that do not terminate at an exterior wall, a firewall or a vertical shaft shall,

(a)	terminate at a vertical fire separation having a fire-resistance rating not less than that required for the floor assembly and extending from the floor assembly to the underside of the floor or roof assembly above, or

(b)	be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11.

(2)  The penetration of a floor assembly by an exit or a vertical service space shall conform to the requirements of Sections 3.4. to 3.6.

(3)  A floor area containing sleeping rooms in a building of Group B, Division 2 or 3 major occupancy shall not be constructed as part of an interconnected floor space.

(4)  Except as permitted in Sentence (5), an elementary or secondary school shall not,

(a)	contain an interconnected floor space, or

(b)	be located in an interconnected floor space.

(5)  An interconnected floor space is permitted in an elementary or secondary school provided,

(a)	the interconnected floor space consists of the first storey, and the storey next above or below it, but not both,

(b)	the interconnected floor space is sprinklered,

(c)	the portions of the upper floor area that do not terminate at an exterior wall, a firewall or a vertical shaft shall terminate at a vertical fire separation extending from the floor assembly to the underside of the floor or roof assembly above,

(d)	except as provided in Clause (e), the fire separation required in Clause (c) need not have a fire-resistance rating,

(e)	where a corridor is located immediately adjacent to the fire separation required in Clause (c), the fire separation shall have a fire-resistance rating of not less than 30 min, and

(f)	where a portion of a floor area is not within the interconnected floor space, the required access to exit from this portion of the floor area shall not lead through the interconnected floor space.

3.2.8.2.  Exceptions to Special Protection

(1)  A mezzanine need not terminate at a vertical fire separation nor be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11. provided the mezzanine,

(a)	serves a Group A, Division 1 major occupancy,

(b)	serves a Group A, Division 3 major occupancy in a building not more than 2 storeys in building height,

(c)	serves a Group A, C, D, E or F major occupancy and the mezzanine conforms to Sentence 3.2.1.1.(3) or (5),

(d)	is not considered a storey in Sentence 3.2.1.1.(4) in calculating building height provided the mezzanine is not more than 500 m2 in area and does not contain a Group B occupancy, or

(e)	is not considered a storey in calculating building height in Sentence 3.2.1.1.(8).

(2)  Except for floors referred to in Sentence 3.1.10.3.(1) and Article 3.2.1.2., openings through a horizontal fire separation for vehicular ramps in a storage garage are not required to be protected with closures and need not conform to this Subsection.

(3)  If a closure in an opening in a fire separation would disrupt the nature of a manufacturing process, such as a continuous flow of material from storey to storey, the closure for the opening is permitted to be omitted provided precautions are taken to offset the resulting hazard.

(4)  An interconnected floor space in a Group B, Division 1 occupancy need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.11. provided the interconnected floor space does not interconnect more than 2 adjacent storeys.

(5)  Except as permitted by Sentence (6), openings for stairways, escalators and inclined moving walks need not conform to the requirements in Articles 3.2.8.3. to 3.2.3.11. provided,

(a)	the opening for each stairway, escalator or walk does not exceed 10 m2,

(b)	the building is sprinklered throughout, and

(c)	the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D or Group E occupancies.

(6)  An interconnected floor space need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.11. provided,

(a)	the interconnected floor space consists of the first storey and the storey next above or below it, but not both,

(b)	the interconnected floor space is sprinklered, and

(c)	the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D, Group E, or Group F, Division 2 or 3 occupancies.

3.2.8.3.  Configuration

(1)  In buildings constructed in conformance with Articles 3.2.8.4. to 3.2.8.11., the unprotected openings through floor assemblies in an interconnected floor space shall be of sufficient size and shall be positioned relative to each other so as to be capable of containing, within the full height of the interconnected floor space, a cylinder conforming to Sentence (2).

(2)  The cylinder referred to in Sentence (1) shall have a cross-section that, where taken at a right angle to the longitudinal axis of such cylinder, is,

(a)	a circle at least 9 m in diameter, or

(b)	an ellipse at least 7 m wide along the minor axis and at least 65 m2 in area.

3.2.8.4.  Exits

(1)  A building that is more than 18 m in height, measured between grade and the floor level of the top storey, and that contains an interconnected floor space, shall be designed to limit the passage of smoke from a fire into exit stairshafts opening into an interconnected floor space so that during a 2 h period after the start of fire, such stairshafts will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis.

(2)  Where a building containing an interconnected floor space is more than 75 m in height, measured between grade and the floor level of the top storey, the exit stairshaft protection required in Sentence (1) shall be accomplished by the provision, between each floor area and each exit stairshaft, of a vestibule provided with a mechanical air supply or with a vent opening to the outdoors.

(3)  Where a vestibule protecting an exit stairshaft is incorporated into the design of the building to meet the requirements of Sentence (1) or (2), such vestibule shall,

(a)	be designed so that each doorway for a door opening into the vestibule is located at least 1 800 mm from a door or doors opening outward from the vestibule,

(b)	be separated from the remainder of the floor area by a fire separation having a fire-resistance rating at least equal to that required for the exit that it serves except that the fire-resistance rating of a fire separation between the vestibule and a public corridor need not exceed 45 min, and

(c)	not have a door or doors opening into more than one exit stairshaft.

(4)  Except where exits serving the floor area are at ground level, the increased travel distance to exits permitted by Clause 3.4.2.5.(1)(c) shall not apply to a floor area within an interconnected floor space.

(5)  Where a portion of a floor area is not within an interconnected floor space, required access to exit from such portion of a floor area shall not lead through an interconnected floor space.

(6)  Except as provided in Sentences (7) and (8), portions of an interconnected floor space that have floor levels more than 18 m above grade shall be served by exits that provide at least 0.3 m2 of area of treads, landings and floor surface for each occupant of such portions of an interconnected floor space.

(7)  The requirements of Sentence (6) need not be applied where a floor area that is a portion of an interconnected floor space and that has a floor level more than 18 m above grade is separated from the remainder of the interconnected floor space by a fire separation having a fire-resistance rating of at least 1 h, except that no fire-resistance rating is required for such fire separation where all of the major occupancies contained within the interconnected floor space may be classified as light hazard occupancies in conformance with Appendix A of NFPA 13 “Installation of Sprinkler Systems”.

(8)  The requirements of Sentence (6) need not be applied where the exit stairs that serve interconnected floor spaces are designed so that the required width of each stair is cumulative.

3.2.8.5.  Elevators

(1)  Except as provided in Sentence (2), where an elevator shaft opens into an interconnected floor space and into storeys that are above such space and that have floor levels more than 18 m above grade, either the elevator doors opening into the interconnected floor space or the elevator doors opening into the storeys above the interconnected floor space shall be protected by vestibules that,

(a)	are designed to restrict the passage of contaminated air to the limit described in Sentence 3.2.8.4.(1), and

(b)	conform to the requirements of Sentence 3.2.8.4.(3).

(2)  Where elevator doors opening into an interconnected floor space are protected by vestibules in conformance with Sentence (1), the elevator doors opening into the lowest storey of the interconnected floor space need not be protected by such vestibules.

3.2.8.6.  Group B Sleeping Rooms

(1)  Openings provided for access between an interconnected floor space and a building or a portion of a building containing Group B major occupancy sleeping rooms shall be provided with vestibules that are provided with a mechanical air supply and that are designed,

(a)	to restrict the passage of smoke from the interconnected floor space into the area containing sleeping rooms in accordance with the limits described in Sentence 3.2.8.4.(1), and

(b)	in conformance with Clause 3.2.8.4.(3)(a).

3.2.8.7.  Sprinklers

(1)  In a building containing an interconnected floor space, storeys that are wholly or partially within an interconnected floor space and all storeys below an interconnected floor space shall be sprinklered.

(2)  In a building containing an interconnected floor space,

(a)	waterflow alarm signals from sprinkler systems shall be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4), and

(b)	sprinkler systems shall be electrically supervised as required in Sentence 3.2.4.9.(2).

3.2.8.8.  Fire Alarm and Detection System

(1)  A building containing an interconnected floor space shall be provided with,

(a)	a fire alarm system and electrically supervised annunciator conforming to Subsection 3.2.4.,

(b)	a system of smoke detectors located,

(i)	on the ceiling of each storey in the vicinity of the openings through floor assemblies described in Article 3.2.8.3., except within dwelling units, heat detectors may be installed instead of smoke detectors, and

(ii)	as required for the activation of the smoke control system described in Sentences (5), (6) and (7) of Article 3.2.8.9., and

(c)	facilities for transmitting a signal to the fire department in conformance with Article 3.2.4.7.

3.2.8.9.  Smoke Control

(1)  A smoke control system conforming to Sentences (2) to (8) shall be designed to control the movement of smoke within a building containing an interconnected floor space.

(2)  The design of the smoke control system shall assume an outdoor temperature equal to the January design temperature on a 2.5% basis.

(3)  Upon activation of the sprinkler system or automatic detection of smoke by at least two smoke detectors in a single zone within an interconnected floor space, the system shall,

(a)	stop air moving fans that provide for the normal exhausting or re-circulating of air in an interconnected floor space,

(b)	activate exit stairshaft protection required in Article 3.2.8.4.,

(c)	activate elevator protection required in Article 3.2.8.5., and

(d)	activate the vestibule air supply required in Sentence 3.2.8.6.(1).

(4)  A building containing an interconnected floor space may be designed so that, in the event of a fire arising in a floor area or part of a floor area within the interconnected floor space, automatic detection of such fire will activate air handling equipment that,

(a)	extracts air directly from such floor area or part of a floor area at the rate of at least 6 air changes per hour, and

(b)	supplies air in sufficient quantities and at appropriate locations to prevent smoke from passing out of such floor area into other portions of the interconnected floor space.

(5)  For purposes of Sentences (6) and (7), the volume of an interconnected floor space need not include the aggregate volume of those floor areas or portions of floor areas designed to have zoned air extraction in accordance with Sentence (4).

(6)  A mechanical exhaust shall be provided to remove air at the top of an interconnected floor space at the rate of at least 6 air changes per hour, except that where the volume of the interconnected floor space exceeds 17 000 m3, only 4 air changes per hour need be provided.

(7)  Except where zoned mechanical exhaust described in Sentence (4) has been activated, upon automatic detection of smoke within the volume of the interconnected floor space, the mechanical exhaust described in Sentence (6) shall be automatically activated and supply air shall be provided in sufficient quantity and at appropriate locations to allow a consistent rate of removal of smoke throughout the volume of the interconnected floor space.

(8)  Overriding manual controls for the smoke control system shall be provided for fire department use at an acceptable location in the vicinity of the fire alarm annunciator.

3.2.8.10.  Emergency Power Supply

(1)  In a building that is more than 18 m in height, measured between grade and the floor level of the top storey, an emergency power supply capable of operating under a full load for at least 2 h shall be provided by an emergency generator or by a separate service not supplied by the same substation as the primary source for fans required for smoke control purposes in Articles 3.2.8.4., 3.2.8.5., 3.2.8.6. and 3.2.8.9.

3.2.8.11.  Testing

(1)  The systems for smoke control and venting described in Articles 3.2.8.4., 3.2.8.5., 3.2.8.6. and 3.2.8.9. shall be tested to ensure satisfactory operation.

3.2.9.  Standpipe Systems

3.2.9.1.  Where Required

(1)  Except as provided in Sentences (4) to (7), a standpipe system shall be installed in every building that,

(a)	is more than 3 storeys in building height,

(b)	is more than 14 m high measured between grade and the ceiling of the top storey, or

(c)	is not more than 14 m high measured between grade and the ceiling of the top storey but has a building area exceeding the area shown in Table 3.2.9.1. for the applicable building height if the building is not sprinklered.

(2)  A standpipe system shall be installed in every basement of a building that requires a standpipe system above grade.

(3)  A standpipe system shall be installed in every basement of a building that is regulated by Sentence 3.2.2.15.(2).

Table 3.2.9.1.
Building Limits without Standpipe Systems

Forming Part of Sentence 3.2.9.1.(1)

| Column 1 | Column 2 | Column 3 | Column 4 |
| --- | --- | --- | --- |
| Occupancy Classification | Building Area, m2 |  |  |
|  | 1 Storey | 2 Storeys | 3 Storeys |
| A | 2 500 | 2 000 | 1 500 |
| C | 2 000 | 1 500 | 1 000 |
| D | 4 000 | 3 000 | 2 000 |
| F, Division 2 | 2 000 | 1 500 | 1 000 |
| F, Division 3 | 3 000 | 2 000 | 1 000 |

(4)  A standpipe system is not required to be installed in the lowest storey in a building if this storey is a service room that has an area not more than 50 m2.

(5)  A standpipe system is not required to be installed in a roof-top enclosure if this enclosure has an area not more than 50 m2.

(6)  A standpipe system is not required to be installed in a storage garage conforming to Article 3.2.2.83. provided the building is not more than 15 m high.

(7)  A standpipe system is not required to be installed in a dwelling unit that,

(a)	extends not more than 3 storeys above adjacent ground level,

(b)	is completely cut off from the remainder of the building so that there is no access to the remainder of the building, and

(c)	has direct access to its interior by means of an exterior doorway located not more than 1 500 mm above or below adjacent finished ground level.

3.2.9.2.  Standpipe System Design

(1)  Except as otherwise provided in this Subsection, if a standpipe system is required, the design, construction, installation and testing of the system shall be in conformance with NFPA 14, “Installation of Standpipe and Hose Systems”.

(2)  A dry standpipe that is not connected to a water supply shall not be considered as fulfilling the requirements of this Article.

(3)  If more than one standpipe is provided, the total water supply need not be more than 30 L/s.

(4)  The residual water pressure at the design flow rate at the hydraulically most remote hose connection of a standpipe system that is required to be installed in a building is permitted to be less than 450 kPa provided that,

(a)	the building is sprinklered,

(b)	the water supply at the base of the sprinkler riser is capable of meeting the design flow rate and pressure demand of the sprinkler system, including the inside and outside hose allowance, and

(c)	fire protection equipment is available to deliver, by means of the fire department connection, the full demand flow rate at a residual water pressure of 450 kPa at the hydraulically most remote hose connection of the standpipe system.

(5)  A fire department connection shall be provided for every standpipe system.

(6)  Pumps required to have a rated net head pressure greater than 280 kPa and their controllers shall be listed and labelled.

(7)  Couplings for hoses or other fittings used in connection with such couplings shall conform to ULC-S513, “Threaded Couplings for 38 mm and 65 mm Fire Hose” or ULC-S543, “Internal Lug Quick Connect Couplings for Fire Hose”.

(8)  If freezing of piping may occur, a dry standpipe system may be provided and so arranged through the use of listed devices to,

(a)	automatically admit water to the system by opening of a hose valve, and

(b)	transmit a signal to an attended location.

(9)  A standpipe riser shall be located in,

(a)	an exit stair shaft, or

(b)	a service space.

3.2.9.3.  Hose Connections

(1)  If a standpipe system is required in a building, 38 mm diam hose connections shall be provided in each storey in the building.

(2)  In addition to the requirements in Sentence (1), if a standpipe system is required, 65 mm diam hose connections shall be installed in each storey in the building if the building,

(a)	is more than 25 m high, measured between grade and the ceiling of the top storey, or

(b)	has a building area of more than 4 000 m2.

3.2.9.4.  Hose Stations

(1)  If a standpipe system is required in a building, hose stations shall be provided in each storey in the building.

(2)  Each hose station shall be equipped with a hose rack filled with not more than 30 m of 38 mm diam fire hose and the hose rack and fire hose shall be,

(a)	listed, or

(b)	approved by the Factory Mutual Research Corporation.

(3)  Except in a Group F occupancy, at each hose station, hose connections, valves, fire hose, nozzle and hose rack shall be in a hose cabinet.

(4)  A hose cabinet referred to in Sentence (3) shall be of sufficient size to,

(a)	contain the equipment referred to in Sentence (3),

(b)	contain a listed fire extinguisher, and

(c)	provide sufficient clearance to permit the use of a standard fire department hose key.

(5)  Hose stations shall be located,

(a)	so that every portion of the building can be reached by a hose stream and is within 3 m of a nozzle attached to the hose required in Sentence (2),

(b)	not more than 5 m from every required exit serving a floor area, except,

(i)	for the first storey, or

(ii)	if additional hose stations are required to achieve full coverage of the floor area, and

(c)	in a conspicuous location where they are not likely to be obstructed.

(6)  Except as permitted in Sentence (7), hose stations shall be located so that it is not necessary to penetrate an exit with a hose in order to provide the design coverage required in Clause (5)(a).

(7)  A hose is permitted to penetrate an exit in order to provide the required coverage to,

(a)	a service room referred to in Sentence 3.2.9.1.(4),

(b)	a roof-top enclosure referred to in Sentence 3.2.9.1.(5),

(c)	a room not more than 50 m2 in area, or

(d)	a room or group of rooms not more than 200 m2 in area in a sprinklered floor area.

(8)  A hose station located on one side of a horizontal exit shall be considered to serve only the floor area on that side of the horizontal exit.

(9)  A hose cabinet shall be located so that its door, when fully opened, will not obstruct the required width of a means of egress.

(10)  A hose station in a Group B, Division 1 major occupancy is permitted to be located in a secure area, or in a lockable cabinet provided that,

(a)	identical keys for all cabinets are located at all guard stations, or

(b)	electrical remote release devices are provided and are connected to an emergency power supply.

3.2.9.5.  Supervisory Signal Annunciation for Valves

(1)  If a fire alarm system in a building is required to have an annunciator by Sentence 3.2.4.8.(1), except for hose valves, each valve controlling water supplies in a standpipe system shall be equipped with an electrically supervised switch for transmitting a signal for individual annunciation in the event of movement of the valve handle.

3.2.9.6.  Water Supply for 38 mm Hose Connections

(1)  If a standpipe and hose system is required, the water supply shall be sufficient to provide a flow, measured at each of the two hydraulically most remote 38 mm diam hose connections,

(a)	of not less than 380 L/min,

(b)	for not less than 30 min,

(c)	at a pressure of not less than 450 kPa, and

(d)	of not less than 190 L/min from each of the two outlets simultaneously.

3.2.9.7.  Water Supply for 65 mm Hose Connections

(1)  If 65 mm diam hose connections are required, the water supply shall be sufficient to provide a flow, measured at each of the two hydraulically most remote 65 mm diam hose connections,

(a)	of not less than 1 890 L/min,

(b)	for not less than 30 min,

(c)	at a pressure of not less than 450 kPa, and

(d)	of not less than 945 L/min from each of the two outlets simultaneously.

(2)  If the building is less than 84 m high, measured between grade and the ceiling level of the top storey, the water supply required in Sentence (1) is permitted to be supplied through the fire department connection.

(3)  If the building is 84 m or more high, measured between grade and the ceiling level of the top storey, the water supply required in Sentence (1) shall be provided by sufficient pumping capacity.

(4)  If the building is 84 m or more high, measured between grade and the ceiling level of the top storey, the building shall be served by no fewer than two sources of water supply from a public water system.

Section 3.3.  Safety Within Floor Areas

3.3.1.  All Floor Areas

3.3.1.1.  Separation of Suites

(1)  Except as permitted by Sentences (2) and (3), each suite in other than business and personal services occupancies shall be separated from adjoining suites by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  Occupancies that are served by public corridors conforming to Clause 3.3.1.4.(4)(b) in a building that is sprinklered, are not required to be separated from one another by fire separations provided the occupancies are,

(a)	suites of business and personal services occupancy,

(b)	fast food vending operations that do not provide seating for customers,

(c)	suites of mercantile occupancy, or

(d)	any combination of these occupancies.

3.3.1.2.  Hazardous Substances, Equipment and Processes

(1)  Except as provided in Subsection 3.3.5., the storage, handling and use of the hazardous substances shall be in conformance with,

(a)	the Fire Code made under the Fire Protection and Prevention Act, 1997, or

(b)	the CCBFC, “National Fire Code of Canada”, in the absence of regulations referred to in Clause (a).

(2)  Cooking equipment, not within a dwelling unit, used in processes producing grease-laden vapours shall be designed and installed in conformance with Part 6.

(3)  A fuel-fired appliance shall not be installed in a corridor serving as an access to exit.

3.3.1.3.  Means of Egress

(1)  Access to exit within floor areas shall conform to Subsections 3.3.2. to 3.3.5., in addition to the requirements of this Subsection.

(2)  If a podium, terrace, platform or contained open space is provided, egress requirements shall conform to the appropriate requirements of Sentence 3.3.1.5.(1) for rooms and suites.

(3)  Means of egress shall be provided from every roof that is intended for occupancy, and from every podium, terrace, platform or contained open space.

(4)  At least two separate means of egress shall be provided from a roof, used or intended for an occupant load more than 60, to stairs designed in conformance with the exit stair requirements of Section 3.4.

(5)  A rooftop enclosure shall be provided with an access to exit that leads to an exit,

(a)	at the roof level, or

(b)	on the storey immediately below the roof.

(6)  A rooftop enclosure that is more than 200 m2 in area shall be provided with at least 2 means of egress.

(7)  Two points of egress shall be provided for a service space referred to in Sentence 3.2.1.1.(9) if,

(a)	the area is more than 200 m2, or

(b)	the travel distance measured from any point in the service space to a point of egress is more than 25 m.

(8)  Except as permitted by Sentences 3.3.4.4.(6) and (7), each suite in a floor area that contains more than one suite shall have,

(a)	an exterior exit doorway, or

(b)	a doorway,

(i)	into a public corridor, or

(ii)	to an exterior passageway.

(9)  Except as permitted by this Section and by Sentence 3.4.2.1.(2), at the point where a doorway referred to in Sentence (8) opens onto a public corridor or exterior passageway, it shall be possible to go in opposite directions to each of 2 separate exits.

(10)  Means of egress from a roof for personnel servicing roof top equipment or for a below ground service room that is not normally occupied, is permitted to be provided by stairways or fixed ladders.

3.3.1.4.  Public Corridor Separations

(1)  Except as otherwise required by this Part or as permitted by Sentence (4), a public corridor shall be separated from the remainder of the storey by a fire separation.

(2)  Except as permitted by Sentence (3) and Clauses (4)(a) and (b), the fire separation between a public corridor and the remainder of the storey shall have a fire-resistance rating not less than 45 min.

(3)  If a storey is sprinklered, no fire-resistance rating is required for a fire separation between a public corridor and the remainder of the storey provided the corridor does not serve a care occupancy or detention occupancy or a residential occupancy.

(4)  No fire separation is required in a sprinklered floor area between a public corridor and,

(a)	except as required by Sentences 3.3.3.5.(10) and 3.3.4.2.(1) and notwithstanding Sentences 3.4.2.4.(2), the remainder of a storey provided the travel distance from any part of the floor area to an exit is not more than 45 m.,

(b)	a room or suite provided the public corridor complies with Sentence 3.3.1.9.(6) and Clause 3.4.2.5.(1)(d), or

(c)	a space containing plumbing fixtures required by Subsection 3.7.4. provided the space and the public corridor are separated from the remainder of the storey by a fire separation that has a fire-resistance rating not less than that required between the public corridor and the remainder of the storey.

(5)  The sprinkler system in Sentences (3) and (4) shall be electrically supervised in conformance with Sentence 3.2.4.9.(2) and, upon operation, shall cause a signal to be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4) when the corridor serves a Group E or Group F, Division 1 or 2 occupancy.

3.3.1.5.  Egress Doorways

(1)  Except for dwelling units, a minimum of 2 egress doorways located so that one doorway could provide egress from the room or suite as required by Article 3.3.1.3. if the other doorway becomes inaccessible to the occupants due to a fire that originates in the room or suite, shall be provided for every room and every suite,

(a)	whose area is more than 15 m2 and is used for,

(i)	a high hazard industrial occupancy, or

(ii)	a hazardous room,

(b)	intended for an occupant load more than 60,

(c)	in a floor area that is not sprinklered if,

(i)	the area of a room or suite is more than the value in Table 3.3.1.5.A., or

(ii)	the travel distance within the room or suite to the nearest egress doorway, is more than the value in Table 3.3.1.5.A.,

(d)	in a floor area that is sprinklered and does not contain a high hazard industrial occupancy if,

(i)	the travel distance to an egress doorway is more than 25 m, or

(ii)	the area of the room or suite is more than the value in Table 3.3.1.5.B., or

(e)	where the area of the room is more than 100 m2 and it is a hazardous classroom in elementary or secondary school.

Table 3.3.1.5.A.
Egress in Floor Area, not Sprinklered

Forming Part of Sentence 3.3.1.5.(1)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Occupancy of Room or Suite | Maximum Area of Room or Suite, m2 | Maximum Distance to Egress Doorway, m |
| Group A | 150 | 15 |
| Group C | 150(1) | 25(1) |
| Group D | 200 | 25 |
| Group E | 200 | 25 |
| Group F, Division 2 | 200 | 25 |
| Group F, Division 3 | 200 | 25 |

Note to Table 3.3.1.5.A.:

(1) See Article 3.3.4.4. for dwelling units.

(2)  Except for a mezzanine within a dwelling unit, every mezzanine that is not required to terminate at a vertical fire separation in Article 3.2.8.2. shall have 2 egress facilities placed in such a manner that one facility could provide egress from the mezzanine if the other facility becomes inaccessible to the occupants of the mezzanine due to a fire that might originate in the room or suite in which the mezzanine is located,

(a)	where the occupancy of the mezzanine, room or suite is classified as Group F, Division 1,

(b)	where the mezzanine is intended for an occupant load of more than 60 persons,

(c)	in a floor area that is not sprinklered if,

(i)	the area of a mezzanine is more than the value in Table 3.3.1.5.A., or

(ii)	the travel distance to an egress doorway or an egress facility is more than the value in Table 3.3.1.5.A., or

(d)	in a floor area that is sprinklered if,

(i)	the travel distance to an egress doorway or an egress facility is more than 25 m, or

(ii)	the area of the mezzanine is more than the value in Table 3.3.1.5.B.

Table 3.3.1.5.B.
Egress in Sprinklered Floor Area

Forming Part of Sentence 3.3.1.5.(1)

| Column 1 | Column 2 |
| --- | --- |
| Occupancy of Room or Suite | Maximum Area of Room or Suite, m2 |
| Group A | 200 |
| Group B, Division 1 | 100 |
| Group B, Division 2 or 3 |  |
| sleeping rooms | 100 |
| other than sleeping rooms | 200 |
| Group C | 150(1) |
| Group D | 300 |
| Group E | 200 |
| Group F, Division 2 | 200 |
| Group F, Division 3 | 300 |

Note to Table 3.3.1.5.B.:

(1) See Article 3.3.4.4. for dwelling units.

(3)  For the purpose of Clause (2)(c) and (d),

(a)	if the room or suite in which the mezzanine is located is permitted to have one egress doorway, the travel distance is measured from any point on the mezzanine to that doorway, or

(b)	if the room or suite in which the mezzanine is located is required to have more than one egress doorway, the travel distance is measured from any point on the mezzanine to the nearest egress facility leading from the mezzanine.

(4)  Except for a mezzanine which is not considered as a storey in calculating building height in Sentence 3.2.1.1.(4), where the space below a mezzanine is enclosed, an egress facility from the mezzanine shall not lead into the enclosed space.

3.3.1.6.  Travel Distance

(1)  If more than one egress doorway is required from a room or suite referred to in Article 3.3.1.5., the travel distance within the room or suite to the nearest egress doorway shall not exceed the maximum travel distances specified in Clauses 3.4.2.5.(1)(a), (b), (c) and (f) for exits.

3.3.1.7.  Protection on Floor Areas with a Barrier-Free Path of Travel

(1)  Except as provided in Sentences (2) and (3), every floor area above or below the first storey that has a barrier-free path of travel shall,

(a)	be served by an elevator,

(i)	conforming to Sentences 3.2.6.9.(4) to (6),

(ii)	protected against fire in conformance with Clause 3.2.6.9.(3)(b) or (c), and

(iii)	in a building over 3 storeys in building height, protected against smoke movement so that the hoistway will not contain more than 1% by volume of contaminated air from a fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Supplementary Standard SB-1, or

(b)	be divided into at least 2 zones by fire separations conforming to Sentences (4) to (6) so that,

(i)	persons with physical disabilities can be accommodated in each zone,

(ii)	the travel distance from any point in one zone to a doorway leading to another zone shall be not more than the value for travel distance permitted by Sentence 3.4.2.5.(1) for the occupancy classification of the zone, and

(iii)	a barrier-free path of travel is provided to an exit.

(2)  In residential occupancies, the requirements of Sentence (1) are waived if a balcony conforming to Sentence (7) is provided for each suite, except for suites on the storey containing the barrier-free entrance described in Article 3.8.1.2.

(3)  The requirements of Sentences (1) and (2) are waived when the building is sprinklered.

(4)  Except as permitted by Sentence (5), the fire separations referred to in Clause (1)(b) shall have a fire-resistance rating not less than 1 h.

(5)  The fire-resistance rating of the fire separations referred to in Clause (1)(b) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(6)  A door acting as a closure in a fire separation referred to in Clause (1)(b) shall be weatherstripped or otherwise designed and installed to retard the passage of smoke.

(7)  A balcony required by Sentence (2) shall,

(a)	be provided with a door way having a clear width of not less that 800 mm when the door is in the open position,

(b)	have no projection above the walking surface more than 13 mm,

(c)	be not less than 1 500 mm deep from the outside face of the exterior wall to the inside edge of the balcony, and

(d)	provide not less than 0.5 m2 for each occupant of the suite.

3.3.1.8.  Headroom Clearance

(1)  Except within the floor area of a storage garage, the minimum headroom clearance in every access to exit shall conform to the requirements of Article 3.4.3.5. for exits.

3.3.1.9.  Corridors

(1)  The minimum width of a public corridor shall be 1 100 mm.

(2)  Except as required by Sentences 3.3.3.3.(2) and (3), the minimum unobstructed width shall be 1 100 mm for every,

(a)	corridor used by the public,

(b)	corridor serving classrooms, and

(c)	corridor in a Group B, Division 2 or 3 occupancy where the corridor

(i)	serves a service room,

(ii)	serves an administrative area,

(iii)	will not be used by non-ambulatory outpatients, or

(iv)	will not be used by non-ambulatory residents.

(3)  Except as permitted by Sentence (4), obstructions located within 1 980 mm of the floor shall not project more than 100 mm horizontally in a manner that would create a hazard for a person with a visual disability traveling adjacent to the walls in,

(a)	an exit passageway,

(b)	a public corridor,

(c)	a corridor used by the public,

(d)	a corridor serving classrooms, or

(e)	a corridor serving patients’ or residents’ sleeping rooms in a Group B, Division 2 or Division 3 occupancy.

(4)  The horizontal projection of an obstruction referred to in Sentence (3) is permitted to be more than 100 mm provided the clearance between the obstruction and the floor is less than 680 mm.

(5)  If a corridor contains an occupancy, the occupancy shall not reduce the unobstructed width of the corridor to less than its required width.

(6)  If a public corridor conforming to Clause 3.4.2.5.(1)(d) contains an occupancy,

(a)	the occupancy shall be located so that for pedestrian travel there is an unobstructed width not less than 3 m at all times adjacent and parallel to all rooms and suites that front onto the public corridor, and

(b)	the combined area of all occupancies in the public corridor shall be not more than 15% of the area of the public corridor.

(7)  Except as provided in Sentence 3.3.3.3.(1), a dead end corridor shall conform to Sentences (8) to (14).

(8)  A dead end corridor is permitted in an assembly occupancy where there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(9)  In a residential occupancy, except for corridors served by a single exit as described in Sentence 3.3.4.4.(7), a dead end public corridor is permitted provided it is not more than 6 m long.

(10)  Dead end corridors in Sentence (9) shall contain no door openings to service rooms containing fuel-fired appliances or rooms that may be considered a hazard.

(11)  A dead end public corridor is permitted in a business and personal services occupancy where,

(a)	the dead end corridor,

(i)	serves an occupant load of not more than 30 persons,

(ii)	is not more than 9 m long, and

(iii)	is provided with doors having self-closing devices, or

(b)	there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(12)  A dead end corridor is permitted in a mercantile occupancy where,

(a)	the dead end corridor,

(i)	serves an occupant load of not more than 30 persons,

(ii)	is not more than 9 m long, and

(iii)	is provided with doors having self-closing devices, or

(b)	there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(13)  A dead end corridor is permitted in a low or medium hazard industrial occupancy where,

(a)	the dead end corridor

(i)	serves an occupant load of not more than 30 persons,

(ii)	is not more than 9 m long, and

(iii)	is provided with doors having self-closing devices, or

(b)	there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(14)  A dead end corridor is permitted in a high hazard industrial occupancy where there is a second and separate egress doorway from each room or suite not leading into a dead end corridor.

(15)  Except as otherwise required by this Section, aisles shall be provided in conformance with the Fire Code made under the Fire Protection and Prevention Act, 1997.

3.3.1.10.  Door Swing

(1)  Except as permitted by Article 3.3.1.11., a door that opens into a corridor or other facility providing access to exit from a suite, or a room not located within a suite, shall swing on a vertical axis.

(2)  Except as permitted by Article 3.3.1.11., a door that opens into a corridor or other facility providing access to exit from a room or suite shall swing in the direction of travel to the exit if the room or suite is used or intended for,

(a)	an occupant load more than 60,

(b)	a high hazard industrial occupancy, or

(c)	a hazardous classroom in an elementary or secondary school.

(3)  Every door that divides a corridor that is not wholly contained within a suite shall swing on a vertical axis in the direction of travel to the exit where the corridor provides access to exit for,

(a)	an occupant load more than 60,

(b)	a high hazard industrial occupancy,

(c)	a hazardous classroom in an elementary or secondary school, or

(d)	a Group B, Division 2 or 3 occupancy.

(4)  If a pair of doors is installed in a corridor that provides access to exit in both directions, the doors shall swing in opposite directions, with the door on the right hand side swinging in the direction of travel to the exit.

3.3.1.11.  Sliding Doors

(1)  Except as permitted by Sentence (2), a sliding door provided in the locations described in Article 3.3.1.10. shall,

(a)	be designed and installed to swing on the vertical axis in the direction of travel to the exit when pressure is applied, and

(b)	be identified as a swinging door by means of a label or decal affixed to it.

(2)  In a Group B, Division 1 occupancy, or in an impeded egress zone in other occupancies, sliding doors used in an access to exit need not conform to Sentence (1) and Article 3.3.1.10.

(3)  Movable partitions used to separate a public corridor from an adjacent business and personal services occupancy or a mercantile occupancy need not conform to Sentence (1) and Sentences 3.3.1.10.(1) and (2) provided the partitions are not located in the only means of egress

3.3.1.12.  Doors and Door Hardware

(1)  A door that opens into or is located within a public corridor or other facility that provides access to exit from a suite shall,

(a)	provide a clear opening of not less than 800 mm if there is only one door leaf,

(b)	in a doorway with multiple leaves, have the active leaf providing a clear opening of not less than 800 mm, and

(c)	not open onto a step.

(2)  A door in an access to exit shall be readily openable in travelling to an exit without requiring keys, special devices or specialized knowledge of the door opening mechanism, except that this requirement does not apply to a door serving a contained use area, or an impeded egress zone, provided the locking devices conform to Sentence (6).

(3)  Except as permitted by Sentence (4), door release hardware shall be operable by one hand and the door shall be openable with not more than one releasing operation.

(4)  An egress door from an individual dwelling unit or from a suite of residential occupancy is permitted to be provided with additional devices that require a releasing operation additional to the main door release hardware, provided the devices are readily operable from the inside without the use of keys, special devices or specialized knowledge.

(5)  Door release hardware shall be installed not more than 1 200 mm above the finished floor.

(6)  An egress door in an access to exit serving a contained use area or an impeded egress zone is permitted to be equipped with locking devices that can be released either locally or remotely in conformance with Sentence (7) or Sentence (8).

(7)  Local locking devices permitted by Sentence (6) shall be operable by a key from both sides of the door.

(8)  Controls for the remote release of door locking devices permitted by Sentence (6) shall be located in an area readily available to security personnel.

(9)  Locking devices permitted by Sentence (6) that are electrically operated shall be,

(a)	designed to operate on emergency power, and

(b)	capable of manual release by security personnel.

(10)  A door in an access to exit is permitted to be equipped with an electromagnetic locking device conforming to Sentence 3.4.6.15.(4), except that this permission does not apply to a door,

(a)	in an elementary or secondary school,

(b)	a door leading from a Group F, Division 1 occupancy, or

(c)	except as provided in Sentence (11), requiring a latch release device by Article 3.3.2.6.

(11)  A door in an access to exit in a gaming premise is permitted to be equipped with an electromagnetic locking device conforming to Sentences 3.4.6.15.(4) and (7).

(12)  Except as required in Article 3.3.3.4., in a Group B, Division 2 or 3 occupancy, every door that opens into or is located within a corridor or other facility that provides access to exit shall comply with Sentences (1) and (2) where the door,

(a)	serves a service room,

(b)	serves an administrative area,

(c)	will not be used by non-ambulatory outpatients,

(d)	is located within a patient’s or resident’s sleeping room, or

(e)	is in a nursing home or home for the aged that will accommodate only ambulatory residents.

3.3.1.13.  Ramps and Stairways

(1)  Except as permitted by Sentence (2), Article 3.3.4.7., and Subsection 3.3.2., ramps and stairways that do not serve as exits shall conform to the dimensional, guard, handrail and slip-resistance requirements for exit ramps and stairways of Sentence 3.4.3.2.(7), and Articles 3.4.3.5., and 3.4.6.1. to 3.4.6.8.

(2)  Ramps and stairways that do not conform to the requirements of Sentence (1) and are intended only for occasional use for servicing equipment and machinery are permitted,

(a)	to serve service rooms and service spaces, and

(b)	in industrial occupancies.

3.3.1.14.  Exterior Passageways

(1)  An exterior passageway leading to a required exit shall conform to the requirements of Section 3.4. for exterior exit passageways.

3.3.1.15.  Curved or Spiral Stairs

(1)  A curved or spiral stair is permitted in a stairway not required as an exit provided the stair has,

(a)	treads with,

(i)	a minimum run not less than 150 mm, and

(ii)	an average run not less than 200 mm, and

(b)	risers in conformance with Sentence 3.4.6.7.(2).

3.3.1.16.  Capacity of Access to Exits

(1)  The capacity of an access to exit shall be based on the occupant load of the portion of the floor area served.

(2)  In an access to exit the required width of ramps with a slope not more than 1 in 8, doorways, and corridors shall be based on not less than 6.1 mm per person.

(3)  In an access to exit the required width of a ramp with a slope more than 1 in 8 shall be based on not less than 9.2 mm per person.

(4)  In an access to exit from a floor area used or intended to be used for patients or residents in a Group B, Division 2 or Division 3 occupancy, the required width of corridors, doorways, and ramps shall be based on not less than 18.4 mm per person.

(5)  The capacity of stairs in an access to exit shall conform to the requirements for stairs in Article 3.4.3.2.(1) to (3).

3.3.1.17.  Guards

(1)  Except as provided in Sentence (6) and Articles 3.3.2.8. and 3.3.4.7., a guard not less than 1 070 mm high shall be provided,

(a)	around each roof to which access is provided for other than maintenance,

(b)	at openings into smoke shafts referred to in Subsection 3.2.6. that are less than 1 070 mm above the floor, and

(c)	at each raised floor, mezzanine, balcony, gallery, interior or exterior vehicular ramp, and at other locations where the difference in level is more than 600 mm.

(2)  Except as provided in Sentence (3) and Sentence 3.3.2.8.(4), openings through any guard that is required by Sentence (1) shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard.

(3)  Openings through any guard that is required by Sentence (1) and that is installed in a building of industrial occupancy shall be of a size which will prevent the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard.

(4)  Openings through any guard that is not required by Sentence (1) and that serves a building of other than industrial occupancy, shall be of a size that,

(a)	will prevent the passage of a sphere having a diameter more than 100 mm, or

(b)	will permit the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings that exceed these limits do not represent a hazard.

(5)  Unless it can be shown that the location and size of openings do not present a hazard, a guard shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level protected by the guard will facilitate climbing.

(6)  Sentence (1) does not apply at the front edges of stages, floor pits in repair garages and loading docks.

3.3.1.18.  Transparent Doors and Panels

(1)  Except for dwelling units and as permitted by Sentence (4), a glass or transparent door shall be designed and constructed so that the existence and position of the door is readily apparent, by attaching non-transparent hardware, bars or other permanent fixtures to it.

(2)  A glass door shall be constructed of,

(a)	laminated or tempered safety glass conforming to CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(b)	wired glass conforming to CAN/CGSB-12.11-M, “Wired Safety Glass”.

(3)  Except as permitted by Sentence (4), transparent panels used in an access to exit that, because of their physical configuration or design, could be mistaken as a means of egress shall be made inaccessible by barriers or railings.

(4)  Sliding glass partitions that separate a public corridor from an adjacent occupancy and that are intended to be open during normal working hours need not conform to Sentences (1) and (3), provided the partitions are suitably marked to indicate their existence and position.

(5)  Glass in doors and in sidelights that could be mistaken for doors, within or at the entrances to dwelling units and in public areas, shall conform to the requirements of Article 9.6.6.2.

(6)  A window in a public area that extends to less than 1 070 mm above the floor and is located above the second storey in a building of residential occupancy, shall be protected by a barrier or railing from the floor to not less than 1 070 mm above the floor, or the window shall be non-openable and designed to withstand the lateral design loads for balcony guards required by Article 4.1.5.15.

3.3.1.19.  Exhaust Ventilation

(1)  An exhaust ventilation system designed in conformance with the appropriate requirements of Part 6 shall be provided in a building or part of a building in which dust, fumes, gases, vapour or other impurities or contaminants have the potential to create a fire or explosion hazard.

(2)  Explosion relief devices, vents or other protective measures conforming to Subsection 6.2.2. shall be provided for a space in which substances or conditions that have the potential to create an explosion hazard are present as a result of the principal use of a building.

3.3.1.20.  Janitors’ Rooms

(1)  Except as permitted by Sentences (2) and (3), a room or space within a floor area for the storage of janitorial supplies shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the room or space is located is sprinklered.

3.3.1.21.  Common Laundry Rooms

(1)  Except as permitted by Sentences (2) and (3), in a building of residential occupancy, a laundry room in a floor area that is not within a dwelling unit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the laundry room is located is sprinklered.

3.3.1.22.  Obstructions

(1)  No obstruction shall be permitted in any occupancy that would restrict the width of a normal means of egress from any part of a floor area to less than 750 mm unless an unobstructed alternative means of egress is provided adjacent to, accessible from, and plainly visible from the obstructed means of egress.

3.3.1.23.  Signs in Service Spaces

(1)  Illuminated signs conforming to Sentences 3.4.5.1.(3) and (5) shall be provided to indicate the direction to egress points in a service space referred to in Sentence 3.2.1.1.(9).

3.3.1.24.  Welding and Cutting

(1)  Except as provided in Sentence (2), welding and cutting operations shall be located in a room,

(a)	separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or

(b)	protected by an automatic fire extinguishing system.

(2)  Sentence (1) does not apply to an industrial occupancy where the welding and cutting operations do not present a fire or explosion hazard to adjacent areas.

3.3.2.  Assembly Occupancy

3.3.2.1.  Scope

(1)  This Subsection applies to assembly occupancies and to outdoor places of assembly.

3.3.2.2.  Fire Separations

(1)  Except as permitted by Sentence (2), the seating area of a Group A, Division 1 occupancy shall be separated from adjacent occupancies in the floor area by a fire separation having a fire-resistance rating not less than 1 h if the occupant load in the seating area exceeds 200.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  If usable space exists under tiers of seats in arena type buildings, a fire separation with a fire-resistance rating not less than 45 min shall be provided between the space and the seats or the space shall be sprinklered.

(4)  Except as required in Sentences (5), (6) and (7), in an elementary or secondary school, a hazardous classroom shall be separated from the remainder of the building by a fire-separation having a fire-resistance rating not less than,

(a)	1 h where the building is not sprinklered, or

(b)	30 min where the building is sprinklered.

(5)  Except as provided in Sentence (6), in an elementary or secondary school, a hazardous classroom containing an auto repair shop shall be separated from the remainder of the building by a fire-separation having a fire-resistance rating not less than,

(a)	2 h where the building is not sprinklered, or

(b)	1 h where the building is sprinklered.

(6)  In an elementary or secondary school, if there is a group of hazardous classrooms or a group of hazardous classrooms and ancillary rooms of a complementary use, the fire separation required by Sentence (4) or (5) need not be provided within the group but the fire separation is required between the group and the remainder of the building.

(7)  In an elementary or secondary school, a hazardous classroom containing a spray painting operation shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than,

(a)	2 h, or

(b)	1 h where the spray painting operation is separated from the classroom by a fire-separation having a fire-resistance rating not less than 1 h.

(8)  Except as required in Sentence (9), in an elementary or secondary school, where the occupant load of a room exceeds 200 persons, the room and any ancillary rooms of a complementary use shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than,

(a)	1 h where the building is not sprinklered, or

(b)	30 min where the building is sprinklered.

(9)  A kitchen shall not be located within the fire compartment required in Sentence (8).

3.3.2.3.  Fixed Seats

(1)  Except for the requirements of Article 3.3.2.7. for bench-type seats and except as required or permitted by Sentence (2) and Articles 3.3.2.9. and 3.3.2.10., fixed seats in places of assembly shall be,

(a)	attached or secured to the floor, platform or platform riser,

(b)	provided with arms and back, and

(c)	arranged in rows having an unobstructed passage not less than 400 mm wide measured horizontally between plumb lines from the backs of the seats in one row and the edges of the furthest forward projection of the seats in the next row in the unoccupied position.

(2)  For fixed seats with backs and with folding tablet arms, the value of 400 mm required by Clause (1)(c) shall be measured when the tablet arms are in the use position, but is permitted to be measured in the stored position provided,

(a)	there are not more than 7 seats between any seat and the nearest aisle,

(b)	the seats are located in a lecture hall or an auditorium used for instructional purposes, and

(c)	the tablet arm, when raised manually to a vertical position, falls by the force of gravity to the stored position.

(3)  Except as permitted by Sentences (4) and (5), aisles shall be located so that there are not more than 7 seats with backs or 20 seats without backs between any seat and the nearest aisle.

(4)  The requirements of Sentence (3) do not apply if,

(a)	egress doorways are provided to serve both ends of rows of seats,

(b)	each doorway referred to in Clause (a) serves not more than 3 rows of seats, and

(c)	each row contains not more than 100 seats.

(5)  The requirements of Sentence (3) do not apply if,

(a)	there are not more than 7 seats between any seat and the nearest aisle, where the seats are served by a single aisle,

(b)	there are not more than 20 seats between any seat and the nearest aisle, where the seats are served by two aisles,

(c)	each row has an unobstructed passage with minimum width of 400 mm plus 6.1 mm for each additional seat above 16 seats in the row, and

(d)	the travel distance is not more than 45 m measured along the path of travel from any seat to an exit or to an egress doorway.

(6)  Seating arrangements that do not conform to the requirements of Sentences (3) to (5) are permitted provided the standard of safety is not reduced and the time required for egress is not increased.

3.3.2.4.  Aisles

(1)  Except as required by Articles, 3.3.2.9. and 3.3.2.10., aisles leading to egress doors or exits shall be provided in conformance with Sentences (2) to (27) in places of assembly that contain fixed seats.

(2)  In this Subsection, a converging aisle is an aisle into which the occupants of 2 or more aisles converge in travelling to an exit.

(3)  An aisle shall terminate at,

(a)	a converging aisle,

(b)	an egress doorway from the seating area, or

(c)	an exit from the seating area.

(4)  A converging aisle shall terminate at,

(a)	an egress doorway from the seating area, or

(b)	an exit from the seating area.

(5)  The minimum clear width of aisles shall be not less than 1 100 mm , except that the width is permitted to be reduced to not less than,

(a)	750 mm if serving not more than 60 seats, and

(b)	900 mm if serving seats on one side only.

(6)  The minimum clear width of each aisle shall be measured at the point in the aisle furthest from,

(a)	an egress doorway referred to in Clause (15)(a),

(b)	an exit referred to in Clause (15)(b), or

(c)	an exit referred to in Sentence (16).

(7)  Except for an aisle serving bleacher seats, where rows of seats discharge into an aisle, the minimum clear width required by Sentence (5) shall be increased by 25 mm for each metre of length of the aisle measured in the direction towards an exit.

(8)  The width of a converging aisle shall be not less than the required width of the widest aisle plus 50% of the total required width of the remaining aisles that it serves.

(9)  If rows of seats discharge directly into the converging aisle, the width required by Sentence (8) shall be increased by 25 mm for each metre of length of the aisle where the rows of seats discharge into the aisle.

(10)  The width of an egress doorway or an exit leading directly from the seating area shall be not less than the required width of the widest aisle or converging aisle plus 50% of the total required width of the remaining aisles and converging aisles that it serves.

(11)  The requirements in Sentences (5) to (10) and (17) do not apply if,

(a)	the minimum clear width of an aisle is in accordance with Article 3.3.1.16., but is not less than 900 mm if serving seats on one side only,

(b)	the minimum clear width of an aisle is in accordance with Article 3.3.1.16., but is not less than 1 200 mm if serving seats on both sides,

(c)	the minimum clear width of a converging aisle is in accordance with Article 3.3.1.16., but not less than the width of the widest aisle leading to the converging aisle,

(d)	the minimum clear width of an exit leading directly from the seating area is in accordance with Article 3.4.3.2.,

(e)	except as provided in Clause (f), the minimum clear width of an egress doorway leading directly from the seating area is in accordance with Article 3.3.1.16., but not less than the required width of the aisle or the converging aisle leading to the doorway, and

(f)	if more than one vomitory is provided,

(i)	the minimum total clear width of the egress doorways leading from one vomitory is not less than the required width of the aisle or the converging aisle leading to the doorways, and

(ii)	the minimum clear width of egress doorways from additional vomitories is in accordance with Article 3.3.1.16.

(12)  Except as provided in Sentences (13) and (14), dead-end aisles shall be not more than 6 m long.

(13)  Dead-end aisles are permitted to be more than 6 m long, but not more than 10 m long if ,

(a)	the seating area is separated from other seating areas and adjacent occupancies, including a corridor serving any seating area, by a fire separation in accordance with Sentences 3.3.2.2.(1) and (2),

(b)	the travel distance is not more than 25 m measured along the path of travel from any seat to an exit, to an egress doorway or to an opening into a vomitory,

(c)	at least one means of egress, comprising not less than 30 per cent of the required exit capacity, is through an exterior exit, an exit stairway or a corridor not containing an occupancy,

(d)	each row served by the dead-end aisle has a minimum unobstructed width of 400 mm plus 6.1 mm for each additional seat above 7 seats in a row, but not more than 550 mm,

(e)	the minimum ceiling height above the seating area is 3 m,

(f)	the activation of a fire detector or a sprinkler head in the seating area will,

(i)	cause the shutdown of the projection system serving the seating area, and

(ii)	turn on the normal lighting in the seating area, and

(g)	the floor area is sprinklered.

(14)  Dead-end aisles are permitted to be more than 10 m long, but not more than 13 m long if,

(a)	the seating area is separated from other seating areas and adjacent occupancies, including a corridor serving any seating area, by a fire separation in accordance with Sentences 3.3.2.2.(1) and (2),

(b)	the travel distance is not more than 25 m measured along the path of travel from any seat to an exit, to an egress doorway or to an opening into a vomitory,

(c)	at least one means of egress, comprising not less than 30 per cent of the required exit capacity, is through an exterior exit, an exit stairway or a corridor not containing an occupancy,

(d)	each row served by a dead-end aisle has a minimum unobstructed width of 400 mm plus 6.1 mm for each additional seat above 7 seats in a row, but not more than 550 mm,

(e)	the activation of a fire detector or a sprinkler head in the seating area will,

(i)	cause the shutdown of the projection system serving the seating area, and

(ii)	turn on the normal lighting in the seating area,

(f)	a voice communication system is installed in conformance with Article 3.2.4.22.,

(g)	a smoke control system is installed to control movement of smoke in the seating area or a smoke exhaust system is provided so that, in the event of detection of smoke by a smoke detector in the seating area, air handling equipment is activated to extract air directly from the seating area at the rate of at least 6 air changes per hour, and

(h)	the floor area is sprinklered.

(15)  Where a seating area is separated as required by Sentences 3.3.2.2.(1) and (2) or 3.3.2.2.(8), the length of travel by any aisle shall be not more than 45 m measured from the most remote point of the aisle to,

(a)	an egress doorway in the required separation, or

(b)	an exit leading directly from the seating area.

(16)  Where a seating area is not required to be separated by Sentences 3.3.2.2.(1) and (2) or 3.3.2.2.(8), the travel distance shall be not more than 45 m measured from the most remote point of the aisle to an exit.

(17)  Side aisles shall be not less than 1 100 mm wide if seating is provided in conformance with Sentence 3.3.2.3.(4).

(18)  An aisle that has a slope not more than 1 in 8 shall not be stepped.

(19)  An aisle that slopes more than 1 in 8 shall be stepped.

(20)  The passageway between rows of seats served by a stepped aisle shall be level at right angles to the line of travel.

(21)  The riser of a step in an aisle shall be,

(a)	not less than 110 mm high, and

(b)	not more than 200 mm high.

(22)  Variations are permitted in riser height provided,

(a)	the height of adjacent risers does not vary by more than 6 mm, and

(b)	the depth of a tread or a platform in the direction of travel is not less than 430 mm.

(23)  Steps in an aisle shall,

(a)	have a run not less than 230 mm exclusive of nosings,

(b)	have a tread depth not less than 250 mm,

(c)	extend to the adjacent rows of seats in a manner that will not create a hazard from tripping, and

(d)	have a finish on the treads conforming to Sentence 3.4.6.1.(1).

(24)  The location of every riser in an aisle shall be made apparent from both directions of travel by strategically placed lighting or contrasting marking stripes.

(25)  A platform in an aisle shall be level, except that a slope not more than 1 in 50 is permitted for a platform that is not less than 430 mm deep in the direction of exit travel.

(26)  If a step is used at the entry to a row of seats from a stepped aisle, an unobstructed platform not less than 800 mm square shall be provided adjacent to the aisle.

(27)  The finish of the surface of a platform in or adjacent to a stepped aisle shall conform to Sentence 3.4.6.1.(1).

3.3.2.5.  Corridors

(1)  Except as permitted by Sentences (2) to (4), a corridor used by the public in an assembly occupancy as an access to exit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  The fire-resistance rating required by Sentence (1) is permitted to be waived if the floor area in which the corridor is located is sprinklered.

(4)  The fire separation required by Sentence (1) is permitted to be waived if the distance from any point in the floor area to an exit measured along the path of travel to an exit does not exceed the travel distance permitted by Article 3.4.2.5.

3.3.2.6.  Doors

(1)  A door equipped with a latching mechanism in an access to exit from a room or suite of assembly occupancy containing an occupant load more than 100 shall be equipped with a device that will release the latch and allow the door to swing wide open when a force not more than that specified in Sentence 3.8.3.3.(7) is applied to the device in the direction of travel to the exit.

3.3.2.7.  Fixed Bench-Type Seats without Arms

(1)  If fixed bench-type seats without arms are provided, the seat width per person shall be assumed to be 450 mm.

(2)  The centre-to-centre spacing between rows of bench-type seats shall be not less than 760 mm if back rests are provided, and not less than 550 mm if back rests are not provided.

(3)  A clear space of not less than 300 mm shall be provided between the back of each seat and the front of the seat immediately behind it.

3.3.2.8.  Guards

(1)  Except as required by Sentences (2) to (4) for bleacher seats, guards shall be installed in outdoor and indoor places of assembly with fixed seats so that,

(a)	at the fascia of every box, balcony or gallery where the seats extend to the edge, the height of guards is not less than,

(i)	760 mm in front of the seats, and

(ii)	920 mm if located at the end of aisles or at the foot of steps,

(b)	the height of guards along every cross aisle other than those adjacent to the fascia of every box, balcony or gallery is not less than 660 mm, except that guards need not be provided if the backs of the seats along the front side of the aisle are not less than 600 mm above the floor of the aisle, and

(c)	where the seating is arranged in successive tiers and the height of rise between platforms is more than 450 mm, the height of guards is not less than 660 mm along the entire row of seats at the edge of the platform.

(2)  The backs and ends of bleacher seats more than 1 200 mm above the ground or floor that are not adjacent to a wall shall be protected with a guard,

(a)	not less than 1 070 mm high above an adjacent aisle surface or foot rest, and

(b)	not less than 920 mm high above the centre of an adjacent seat board.

(3)  If the front of a bleacher is more than 600 mm above the ground or floor, it shall be protected with a guard not less than 840 mm high above the front foot rest.

(4)  Openings through any guard that is required by Sentences (2) and (3) shall be of a size that will prevent the passage of a sphere having a diameter more than 300 mm.

3.3.2.9.  Outdoor Places of Assembly

(1)  A Group A, Division 4 occupancy and each tier or balcony that has a capacity of more than,

(a)	1 000 persons shall have no fewer than 3 separate exits, or

(b)	4 000 persons shall have no fewer than 4 separate exits.

(2)  In a Group A, Division 4 occupancy, every seat shall be located so that the travel distance is not more than 45 m measured along the path of travel from the seat to,

(a)	the ground,

(b)	an exit,

(c)	an opening to a passageway leading from the seating area, or

(d)	a portal, a vomitory or any other opening through the seating deck structure.

(3)  Exits from outdoor stadia or grandstands shall be located not more than 25 m apart.

(4)  The capacity of a means of egress for a Group A, Division 4 occupancy shall conform to the requirements of Sentence 3.4.3.2.(3).

(5)  Aisles in a Group A, Division 4 occupancy,

(a)	shall be located so that there are not more than 20 seats between any seat and the nearest aisle and

(b)	shall be not less than 1 200 mm wide, except that an aisle serving less than 60 persons is permitted to be 750 mm wide

3.3.2.10.  Bleachers

(1)  Steps provided in aisles of bleachers of the telescopic type shall,

(a)	have risers not more than 250 mm high, and

(b)	have treads with a run not less than 280 mm.

(2)  If the vertical distance between seating platforms in bleachers is more than 280 mm, an intermediate step shall be provided the full width of the aisle and proportioned to provide 2 equal risers between platforms.

(3)  If the vertical distance between seating platforms in bleachers is more than 450 mm, 2 intermediate steps shall be provided the full width of the aisle so that there are 3 equal risers between platforms.

(4)  If the passageway between rows of seats is not a closed deck, footboards shall be provided so that,

(a)	the total width of the footboards shall be not less than three quarters of the centre-to-centre spacing between rows of seats, and

(b)	the spacing between footboard members shall be not more than 25 mm.

(5)  Openings above footboards and below the seats in rows of bleachers shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm.

3.3.2.11.  Libraries

(1)  Except as permitted by Sentence (2), a library book storage room that is not normally accessible to the public shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h if it,

(a)	is more than 250 m2 in area, or

(b)	contains book stacks that,

(i)	are more than 10 m high, or

(ii)	penetrate more than one floor assembly.

(2)  The fire separation required by Sentence (1) is not required if the book storage room is sprinklered.

(3)  Open book shelves are permitted above and below a mezzanine floor in a library building provided the height of the shelves is not more than 2 100 mm but not more than 75% of the floor-to-ceiling height of the space above or below the mezzanine floor assembly.

3.3.2.12.  Stages for Theatrical Performances

(1)  A stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be sprinklered.

(2)  A fire separation with a fire-resistance rating not less than 1 h shall be provided between a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas.

(3)  Except as permitted by Sentence (6), a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be separated from the seating area by a fire separation having a fire-resistance rating not less than 1 h, except for a proscenium opening protected with,

(a)	a sprinkler deluge system conforming to the requirements of NFPA 13 “Installation of Sprinkler Systems”,

(b)	an unframed fire curtain if the opening is not more than 20 m wide, or

(c)	a semi-rigid fire curtain if the opening is more than 20 m wide.

(4)  A fire curtain required by Sentence (3) shall be of a type designed to close,

(a)	automatically upon the actuation of the sprinkler system,

(b)	automatically upon actuation of the fire alarm system,

(c)	manually by remote control devices located at the curtain control panel and at each side of the stage, and

(d)	automatically by heat-actuated devices.

(5)  At least 2 vents for the purpose of venting fire and smoke to the outside of a building shall be provided above a stage designed for theatrical performances and shall,

(a)	have an aggregate area not less than one eighth of the area of the stage behind the proscenium opening, and

(b)	be arranged to open automatically upon actuation of the sprinkler system.

(6)  The fire separation referred to in Sentence (3) is not required between a stage and a seating area in a floor area that is sprinklered, provided a sprinkler deluge system is installed at the boundary between the stage and the seating area.

3.3.2.13.  Risers for Stairs

(1)  In a Group A, Division 2 occupancy used for the serving of food and beverages, an interior flight of stairs with fewer than 3 risers is permitted provided it,

(a)	is not less than 900 mm wide,

(b)	is illuminated at all times that occupants are on the premises, and

(c)	has a handrail on each side.

3.3.3.  Care or Detention Occupancy

3.3.3.1.  Scope

(1)  This Subsection applies to care or detention occupancies.

3.3.3.2.  Fire Separations

(1)  The fire separation required by Sentence 3.3.5.5.(1) between a care or detention occupancy and a repair garage shall have no openings.

(2)  Except as permitted by Sentence (4), in a Group B, Division 3 occupancy, walls between sleeping rooms and adjacent rooms shall be constructed as fire separations having a fire-resistance rating not less than 1 h, except that the fire-resistance rating need not be more than 45 min where the floor assembly is not required to be more than 45 min.

(3)  Except as permitted by Sentence (4), in a Group B, Division 3 occupancy, walls separating corridors serving sleeping rooms from adjacent rooms shall be constructed as fire separations having a fire-resistance rating not less than 1 h, except that the fire-resistance rating need not be more than 45 min where the floor assembly is not required to be more than 45 min.

(4)  The walls separating sleeping rooms from adjacent rooms and corridors in those parts of a floor area classified as a Group B, Division 3 occupancy shall be constructed as fire separations but are not required to have a fire-resistance rating if,

(a)	those parts of the floor area contain sleeping accommodation for not more than 10 persons, and

(b)	not more than six occupants require assistance in evacuation in case of an emergency.

(5)  The door in the fire-separation required in Sentence (4) is permitted to be equipped with a roller latch and need to be provided with a self-closing device.

3.3.3.3.  Corridors

(1)  A corridor used by the public or serving patients or residents shall have no dead-end portion unless the area served by the dead-end portion has a second and separate means of egress.

(2)  A corridor serving patients in a hospital shall be not less than 2 400 mm wide.

(3)  Except as permitted in Sentence (5), a corridor serving residents who are not ambulatory in a Group B, Division 2 or 3 occupancy shall be not less than 1 650 mm wide.

(4)  Paired doors in a corridor serving patients or residents shall,

(a)	swing in opposite directions, the right hand door swinging in the direction of travel, and

(b)	be not less than 1 100 mm wide.

(5)  A corridor in a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants require assistance in evacuation in case of an emergency need not comply with Sentence (3).

3.3.3.4.  Doorway Width

(1)  Except as permitted in Sentence 3.3.1.12.(12), the minimum clear width of doorways serving patients or residents shall be 1 050 mm.

3.3.3.5.  Hospitals and Nursing Homes

(1)  Floor areas containing patients’ or residents’ sleeping rooms in a hospital or nursing home shall conform to Sentences (2) to (12).

(2)  Except as permitted by Sentence (3), a floor area containing patients’ or residents’ sleeping rooms in a hospital or nursing home shall be divided into no fewer than 2 fire compartments, each not more than 1 000 m2 in area.

(3)  The floor area on either side of a horizontal exit conforming to Article 3.4.6.9. is permitted to be considered as a fire compartment in applying the requirements of this Article.

(4)  Except as permitted by Sentence (5), fire separations separating fire compartments required by Sentence (2) shall have a fire-resistance rating not less than 1 h.

(5)  The fire-resistance rating of a fire separation referred to in Sentence (4) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(6)  A closure in a fire separation between fire compartments referred to in Sentence (2) shall be weatherstripped or otherwise designed and installed to retard the passage of smoke.

(7)  The travel distance from any point within each fire compartment referred to in Sentence (2) to a door to an adjoining fire compartment shall be not more than 45 m.

(8)  Each fire compartment referred to in Sentence (2) shall be capable of accommodating, in addition to its own occupants, the occupants of the largest adjacent fire compartment based on a clear floor space of 2.5 m2 per patient or resident in the adjacent fire compartment.

(9)  Except as permitted by Sentences (10) and (12), walls between patients’ or residents’ sleeping rooms and the remainder of the floor area shall be constructed as fire separations but are not required to have a fire-resistance rating unless a fire-resistance rating is required by other provisions in this Part.

(10)  The fire separation requirements of Sentence (9) do not apply to walls within a group of intercommunicating patients’ or residents’ rooms, provided the group of rooms does not

(a)	contain more than 5 patients or residents, or

(b)	include storage, bathing or toilet facilities serving persons not occupying the group of rooms.

(11)  A door in a fire separation required by Sentence (9) is permitted to be equipped with a roller latch.

(12)  A fire separation required by Sentence (9) shall not contain any grilles, louvres or other openings.

3.3.3.6.  Protection for Special Care and Treatment Facilities

(1)  Compartments containing rooms such as operating rooms, recovery rooms, delivery rooms, intensive care units and critical care units, from which it is impracticable to move patients in an emergency, shall be,

(a)	separated from adjacent spaces by fire separations having a fire-resistance rating not less than 1 h, and

(b)	provided with a mechanical air supply so that during a period of 2 h after the start of a fire in another space, the compartments will not contain more than 1% by volume of contaminated air from the fire area.

3.3.3.7.  Contained Use Areas

(1)  A contained use area shall conform to Sentences (2) to (5).

(2)  A contained use area shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(3)  Except as permitted by Sentence (4), a building that includes a contained use area shall be sprinklered.

(4)  A contained use area, in a building for which Articles 3.2.2.20. to 3.2.2.83. do not require the installation of an automatic sprinkler system, is not required to be sprinklered as required by Sentence (3) provided,

(a)	the building is designed so that during a period of 2 h after the start of a fire in the contained use area, other fire compartments will not contain more than 1% by volume of contaminated air from the contained use area,

(b)	the building is designed so that during a period of 2 h after the start of a fire in another part of the building, the contained use area will not contain more than 1% by volume of contaminated air from the other part of the building,

(c)	all doors are designed to be remotely released in conformance with Sentence 3.3.1.12.(6), and

(d)	the contained use area does not contain any rooms lined with combustible padding.

(5)  A corridor serving a contained use area shall have no dead-end portion unless the area served by the dead-end portion has a second and separate means of egress.

3.3.3.8.  Handrails

(1)  Corridors and ramps used by residents in a nursing home shall be equipped with handrails on each side conforming to Sentences 3.4.6.4.(3), (4), (6), (7) and (8).

3.3.4.  Residential Occupancy

3.3.4.1.  Scope

(1)  This Subsection applies to residential occupancies.

3.3.4.2.  Fire Separations

(1)  Except as permitted by Sentences (2) and 3.2.2.9.(2), suites of residential occupancy shall be separated from each other and the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(2)  The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

(3)  Floor assemblies within a dwelling unit need not be constructed as fire separations provided,

(a)	the distance between the lowest floor level and the uppermost floor level within the dwelling unit is not more than 6 m, and

(b)	the dwelling unit is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than,

(i)	45 min if the building is sprinklered and is not more than 3 storeys in building height,

(ii)	1 h if the building is sprinklered and is more than 3 storeys in building height

(iii)	1 h if the building is not sprinklered and is not more than 6 storeys in building height, or

(iv)	2 h if the building is not sprinklered and is more than 6 storeys in building height.

(4)  The fire-resistance rating of the fire separation located between a dwelling unit and an attached storage garage need not conform to that required by Sentence 3.3.5.6.(1) provided,

(a)	the storage garage contains not more than 5 vehicles,

(b)	the dwelling unit and the attached storage garage are sprinklered,

(c)	the dwelling unit is separated from the remainder of the building in conformance with Sentences (1) to (3),

(d)	there are no air duct systems connecting the storage garage and the dwelling unit,

(e)	the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and

(f)	every door between the storage garage and the dwelling unit is,

(i)	tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes,

(ii)	fitted with a self-closing device, and

(iii)	not located in a room intended for sleeping.

(5)  The fire separation required by Sentence 3.3.5.6.(1) is not required between a dwelling unit and an attached storage garage, serving that dwelling unit only, provided,

(a)	the dwelling unit and its attached storage garage are separated from the remainder of the building in conformance with Sentences (1) to (3),

(b)	there are no air duct systems connecting the storage garage and the dwelling unit,

(c)	the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and

(d)	every door between the storage garage and the dwelling unit is,

(i)	tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes,

(ii)	fitted with a self-closing device, and

(iii)	not located in a room intended for sleeping.

3.3.4.3.  Storage Rooms

(1)  Sprinklers shall be installed in a storage room provided for the use of tenants in a residential occupancy within a floor area but not contained within a suite.

(2)  Except as permitted by Sentence (3), a storage room referred to in Sentence (1) shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(3)  The fire-resistance rating of the fire separation required by Sentence (2) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for,

(a)	the floor assembly above the floor area, or

(b)	the floor assembly below the floor area, if there is no floor assembly above.

3.3.4.4.  Egress from Dwelling Units

(1)  Single storey dwelling units in an apartment building need not lead to a public corridor or exterior passageway on the same storey provided the dwelling units are served by private stairways leading directly to a public access to exit on the storey,

(a)	immediately above, and

(b)	immediately below.

(2)  Except as permitted by Sentences (3) to (5), a dwelling unit containing more than one storey shall have an exit door or an egress door opening directly into a public access to exit from the uppermost storey and from the lowest storey of the dwelling unit so that each storey is served by an exit or egress door located not more than 1 500 mm above or below its floor level.

(3)  A single exit is permitted from a dwelling unit provided the exit is an exterior doorway not more than 1 500 mm above adjacent ground level and,

(a)	it is not necessary to travel up or down more than one storey to reach the exit door, or

(b)	the uppermost floor level opens to a balcony not more than 6 m above adjacent ground level.

(4)  An egress door from either the uppermost storey or the lowest storey in a dwelling unit, as required in Sentence (2), need not be provided,

(a)	if that storey is served by a stairway that,

(i)	leads to a public access to exit,

(ii)	has no direct access to any other storey in the dwelling unit, and

(iii)	is separated from the other storeys in the dwelling unit by a fire separation having a fire-resistance rating of not less than 45 min,

(b)	if the dwelling unit has not more than 2 storeys above the first storey of the building, or

(c)	if it is not necessary to travel either more than 18 m, or more than 1 storey up or down to reach the egress door.

(5)  An egress door from either the uppermost storey or the lowest storey in a dwelling unit, as required in Sentence (2), need not be provided,

(a)	on the uppermost storey of a dwelling unit having not more than 2 storeys above the first storey of the building,

(b)	on each storey from which it is not necessary to travel either more than 18 m or more than 1 storey up or down within the dwelling unit to reach an egress door, or

(c)	where that storey is,

(i)	provided with a balcony conforming to Sentence (8),

(ii)	not more than 2 storeys above or below the dwelling unit egress door, and

(iii)	in a building that is not more than 6 storeys in building height.

(6)  In a building of residential occupancy not more than 3 storeys in building height, a doorway from a dwelling unit is permitted to open directly into an exit stairway provided the dwelling unit has a second and separate means of egress.

(7)  If a dwelling unit has a second and separate means of egress, one means of egress from a dwelling unit is permitted to pass through,

(a)	an interior corridor served by a single exit,

(b)	an exterior balcony served by a single exit stairway, or

(c)	an exterior passageway served by a single exit stairway.

(8)  Where a balcony is provided to meet the requirements of Sentence (3) or (5), the balcony shall have,

(a)	a solid floor having a fire-resistance rating not less than that required for a floor assembly between suites, and

(b)	an area providing not less than 1.5 m2 per suite occupant, based on occupant load, and a minimum dimension of 1 200 mm.

3.3.4.5.  Automatic Locking Prohibition

(1)  Except for hotels, a door opening onto a public corridor that provides access to exit from a suite shall be designed not to lock automatically.

3.3.4.6.  Sound Transmission

(1)  Sound transmission class ratings of building assemblies shall conform to Section 5.9.

3.3.4.7.  Stairs, Handrails and Guards for Dwelling Units

(1)  Stairs, handrails and guards within a dwelling unit shall conform to the appropriate requirements in Section 9.8.

3.3.4.8.  Stud Wall Reinforcement

(1)  If wood wall studs or sheet steel wall studs enclose the main bathroom in a dwelling unit, reinforcement shall be installed to permit the future installation of a grab bar on a wall adjacent to,

(a)	a water closet in the location required by Clause 3.8.3.8.(1)(d), and

(b)	a shower or bathtub in the location required by Clause 3.8.3.13.(1)(f).

3.3.5.  Industrial Occupancy

3.3.5.1.  Scope

(1)  This Subsection applies to industrial occupancies.

3.3.5.2.  Fire Extinguishing Systems

(1)  In addition to other requirements in this Division for the installation of automatic fire extinguishing systems, an appropriate fire extinguishing system shall be installed in every industrial occupancy floor area to provide protection if required by,

(a)	the Fire Code made under the Fire Protection and Prevention Act, 1997, or

(b)	the CCBFC, “National Fire Code of Canada”, in the absence of provisions referred to in Clause (a).

3.3.5.3.  Basements

(1)  A basement shall not be used for the storage, manufacture or handling of volatile solids, liquids or gases that generate explosive air-vapour mixtures or for processes that involve explosive dusts.

(2)  Entrances and exits to a basement and to rooms containing building services shall be separate from the remainder of the building in a building in which,

(a)	the storage, manufacture or handling of volatile materials can generate explosive air-vapour mixtures, or

(b)	processes occur that produce explosive dusts.

(3)  Basements and rooms referred to in Sentence (2) shall be separated from the remainder of the building with a vapour-tight separation.

3.3.5.4.  Repair and Storage Garages

(1)  If access is provided from a storage garage to a stair tower or elevator serving occupancies above the level of the storage garage, the access shall be through a vestibule conforming to Sentence 3.3.5.7.(3).

(2)  Treads and landings in interior stairs that extend to the roof of a storage garage shall be designed to be free of accumulations of ice and snow.

(3)  A mechanical storage garage not more than 4 storeys in building height, in which no persons other than parking attendants are permitted above the street floor level, need not have a fire separation between the exits and the remainder of the building.

(4)  A garage shall be provided with natural or mechanical ventilation in conformance with the requirements of Subsection 6.2.2. to prevent excessive accumulation of carbon monoxide, exhaust fumes or flammable and toxic vapours.

(5)  Except as required by Sentence 3.8.2.2.(2), the clear height in a storage garage shall be not less than 2000 mm.

(6)  A continuous curb not less than 150 mm high and a guard not less than 1 070 mm high shall be provided at every garage floor opening and around the perimeter of every floor where the exterior walls are omitted.

(7)  Except for open-air storeys, every storey of a storage garage or repair garage located below grade shall be sprinklered.

3.3.5.5.  Repair Garage Separation

(1)  A repair garage and any ancillary spaces serving it, including waiting rooms, reception rooms, tool and parts storage areas and supervisory office space, shall be separated from other occupancies by a fire separation having a fire-resistance rating not less than 2 h.

3.3.5.6.  Storage Garage Separation

(1)  Except as permitted by Sentences 3.3.4.2.(4) and (5), a storage garage shall be separated from other occupancies by a fire separation with a fire-resistance rating not less than 1.5 h.

3.3.5.7.  Vestibules

(1)  If access is provided through a fire separation between a storage garage and a Group A, Division 1 or Group B occupancy, the access shall be through a vestibule conforming to Sentence (3).

(2)  In a building more than 3 storeys in building height, access through a fire separation between a storage garage and a Group A, Division 2, 3 or 4, or a Group C occupancy, shall be through a vestibule conforming to Sentence (3).

(3)  If access is provided through a vestibule, as required by Sentences (1), (2) and 3.3.5.4.(1), the vestibule shall,

(a)	be not less than 1 800 mm long,

(b)	be ventilated,

(i)	naturally to outside air by a vent that has an unobstructed area of not less than 0.1 m2 for each door that opens into the vestibule but not less than 0.4 m², or

(ii)	mechanically at a rate of 14 m3/h for each square metre of vestibule floor surface area, and

(c)	have openings between the vestibule and an adjoining occupancy provided with self-closing doors with no hold-open devices.

3.3.5.8.  Toe-Boards Required

(1)  Where tools or other objects could fall from the floor of an upper level to a lower level in a room or space intended for use as a Group F occupancy, the edge of the floor at the upper level shall be provided with a toe-board extending from the floor surface to a height at least 125 mm above the floor surface.

Section 3.4.  Exits

3.4.1.  General

3.4.1.1.  Scope

(1)  Exit facilities complying with this Section shall be provided from every floor area that is intended for occupancy.

3.4.1.2.  Separation of Exits

(1)  Except as permitted by Sentence (2), if more than one exit is required from a floor area, each exit shall be separate from every other exit leading from that floor area.

(2)  If more than 2 exits are provided from a floor area, exits are permitted to converge in conformance with Sentence 3.4.3.1.(2), provided the cumulative capacity of the converging exits does not contribute more than 50% of the total required exit width for the floor area.

3.4.1.3.  Access to Exits

(1)  Access to exits shall conform to Section 3.3.

3.4.1.4.  Types of Exit

(1)  Subject to the requirements of this Section, an exit from any floor area shall be one of the following, used singly or in combination:

(a)	an exterior doorway,

(b)	an exterior passageway,

(c)	an exterior ramp,

(d)	an exterior stairway,

(e)	a fire escape (conforming to Subsection 3.4.7.),

(f)	a horizontal exit,

(g)	an interior passageway,

(h)	an interior ramp, or

(i)	an interior stairway.

3.4.1.5.  Exterior Exit Passageways

(1)  Access to an exterior exit passageway from a floor area shall be through exit doors at the floor level.

(2)  Every exterior exit passageway that has a drop of more than 500 mm on any side shall have guards on the open sides not less than 1 070 mm high.

3.4.1.6.  Restricted Use of Horizontal Exits

(1)  Except as permitted by Sentence (2), horizontal exits shall not comprise more than one half of the required number of exits from any floor area.

(2)  In a hospital or nursing home, horizontal exits serving patients’ or residents’ sleeping rooms shall comprise not more than two thirds of the required number of exits from any floor area.

(3)  Where an elementary or secondary school is subdivided by a firewall, a horizontal exit shall not serve as an exit but is permitted to serve as an access to exit.

3.4.1.7.  Slide Escapes

(1)  A slide escape shall not be erected on any building as a required exit, but is permitted to be provided as an additional egress facility if unusual hazards are foreseen.

3.4.1.8.  Transparent Doors and Panels

(1)  Glass and transparent panels in an exit shall conform to the appropriate requirements of Article 3.3.1.18. for glass and transparent panels in an access to exit.

3.4.1.9.  Mirrors near Exits

(1)  No mirror shall be placed in or adjacent to any exit in a manner that would confuse the direction of exit.

3.4.1.10.  Combustible Glazing in Exits

(1)  Combustible glazing is not permitted in wall or ceiling assemblies or in closures used to construct an exit enclosure.

3.4.1.11.  Exterior Stairway for Nursing Home

(1)  No open exterior stairway shall serve as a means of egress for residents above the second floor of a nursing home.

3.4.2.  Number and Location of Exits from Floor Areas

3.4.2.1.  Minimum Number of Exits

(1)  Except as permitted by Sentences (2) to (4) and (6), every floor area intended for occupancy shall be served by at least 2 exits.

(2)  A floor area in a building not more than 2 storeys in building height, is permitted to be served by one exit provided the total occupant load served by the exit is not more than 60 and,

(a)	in a floor area that is not sprinklered, the floor area and the travel distance are not more than the values in Table 3.4.2.1.A., or

(b)	in a floor area that is sprinklered,

(i)	the travel distance is not more than 25 m, and

(ii)	the floor area is not more than the value in Table 3.4.2.1.B.

Table 3.4.2.1.A.
Criteria for One Exit, Floor Area not Sprinklered

Forming Part of Sentence 3.4.2.1.(2)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Occupancy of Floor Area | Maximum Floor Area, m2 | Maximum Travel Distance, m |
| Group A | 150 | 15 |
| Group C | 100 | 15 |
| Group D | 200 | 25 |
| Group E | 150 | 15 |
| Group F, Division 2 | 150 | 10 |
| Group F, Division 3 | 200 | 15 |

(3)  Except as permitted by Sentence (4), if Sentence (2) permits a single exit from a floor area classified as Group B or Group C occupancy, the exit shall be an exterior doorway not more than 1 500 mm above adjacent ground level.

Table 3.4.2.1.B.
Criteria for One Exit, Floor Area Sprinklered

Forming Part of Sentence 3.4.2.1.(2)

| Column 1 | Column 2 |
| --- | --- |
| Occupancy of Floor Area | Maximum Floor Area, m2 |
| Group A | 200 |
| Group B | 100 |
| Group C | 150 |
| Group D | 300 |
| Group E | 200 |
| Group F, Division 2 | 200 |
| Group F, Division 3 | 300 |

(4)  The requirements of Sentences (1) and (2) are permitted to be waived for dwelling units having access to exit conforming to Sentences 3.3.4.4.(1) to (4).

(5)  Exits are not required directly from rooftop enclosures that are provided with access to exits in conformance with Sentences 3.3.1.3.(5) and (6).

(6)  Every room containing an assembly occupancy serving a hotel, and located in the building containing the hotel, shall be provided with no fewer than,

(a)	3 separate egress doorways from the room where the occupant load is more than 600 persons, and

(b)	4 separate egress doorways from the room where the occupant load is more than 1000 persons.

(7)  Each egress doorway in Sentence (6) shall be considered as contributing not more than,

(a)	one third of the required width where 3 egress doorways are required, and

(b)	one fourth of the required width where 4 egress doorways are required.

3.4.2.2.  Mezzanine Exiting

(1)  Except as permitted by Sentences (2) to (4), a mezzanine shall be provided with exits on the same basis as required for floor areas by this Section.

(2)  A mezzanine need not conform to Sentence (1) provided Article 3.2.8.1. does not require it to terminate at a vertical fire separation.

(3)  In a floor area that is not sprinklered, a mezzanine need not conform to Sentence (1) where Article 3.2.8.1. does require it to terminate at a vertical fire separation provided the total occupant load of the mezzanine is not more than 60 and,

(a)	the area of the mezzanine does not exceed the area limits for rooms and suites in Table 3.3.1.5.A., and

(b)	the distance limits in Table 3.3.1.5.A. are not exceeded from any point on the mezzanine to,

(i)	the egress doorway from the room in which the mezzanine is located if that room has a single egress doorway, or

(ii)	an egress facility leading from the mezzanine if the room in which the mezzanine is located has 2 egress doorways provided in conformance with Subsection 3.3.1.

(4)  In a floor area that is sprinklered, a mezzanine need not conform to Sentence (1) where Article 3.2.8.1. does require it to terminate at a vertical fire separation provided the total occupant load of the mezzanine is not more than 60 and,

(a)	the area of the mezzanine does not exceed the area limits for rooms and suites in Table 3.3.1.5.B., and

(b)	the distance of travel is not more than 25 m when measured from any point on the mezzanine to,

(i)	the egress doorway from the room in which the mezzanine is located if that room has a single egress doorway, or

(ii)	an egress facility leading from the mezzanine if the room in which the mezzanine is located has 2 egress doorways provided in conformance with Subsection 3.3.1.

3.4.2.3.  Distance between Exits

(1)  Except as provided in Sentence (2), the least distance between 2 required exits from a floor area shall be,

(a)	one half the maximum diagonal dimension of the floor area, but need not be more than 9 m for a floor area having a public corridor, or

(b)	one half the maximum diagonal dimension of the floor area, but not less than 9 m for all other floor areas.

(2)  Exits need not comply with Sentence (1) where,

(a)	the floor area is divided so that not less than one third of the floor area is on each side of the fire separation, and

(b)	it is necessary to pass through the fire separation to travel from one exit to another exit.

(3)  The minimum distance between exits referred to in Sentence (1) shall be the shortest distance that smoke would have to travel between the exits, assuming that the smoke will not penetrate an intervening fire separation.

3.4.2.4.  Travel Distance

(1)  Except as permitted by Sentence (2), for the purposes of this Subsection, travel distance means the distance from any point in the floor area to an exit measured along the path of travel to the exit.

(2)  The travel distance from a suite or a room not within a suite is permitted to be measured from an egress door of the suite or room to the nearest exit provided,

(a)	the suite or room is separated from the remainder of the floor area by a fire separation,

(i)	having a fire-resistance rating not less than 45 min in a floor area that is not sprinklered, or

(ii)	that is not required to have a fire-resistance rating, in a floor area that is sprinklered, and

(b)	the egress door opens onto,

(i)	an exterior passageway,

(ii)	a corridor used by the public that is separated from the remainder of the floor area in conformance with the requirements in Article 3.3.1.4. for the separation of public corridors, or

(iii)	a public corridor that is separated from the remainder of the floor area in conformance with Article 3.3.1.4.

(3)  Travel distance to an exit shall be not more than 50 m from any point in a service space referred to in Sentence 3.2.1.1.(9).

(4)  If there is a firewall in an elementary or secondary school, the travel distance shall not be measured to a door in the firewall, but shall be measured to an exterior exit door or an exit door to a stairway.

3.4.2.5.  Location of Exits

(1)  Except as permitted by Sentences (2), 3.2.8.4.(4) and 3.3.2.4.(13) to (16), if more than one exit is required from a floor area, the exits shall be located so that the travel distance to at least one exit shall be not more than,

(a)	25 m in a high hazard industrial occupancy,

(b)	40 m in a business and personal services occupancy,

(c)	45 m in a floor area that contains an occupancy other than a high hazard industrial occupancy, provided it is sprinklered,

(d)	105 m in any floor area, served by a public corridor, in which rooms and suites are not separated from the remainder of the floor area by a fire separation, provided,

(i)	the public corridor is not less than 9 m wide,

(ii)	the ceiling height in the public corridor is not less than 4 m above all floor surfaces,

(iii)	the building is sprinklered, and

(iv)	not more than one half of the required egress doorways from a room or suite open into the public corridor if the room or suite is required to have more than one egress doorway,

(e)	60 m in any storage garage that conforms to the requirements of Article 3.2.2.83., and

(f)	30 m in any floor area other than those referred to in Clauses (a) to (e).

(2)  Except for a high hazard industrial occupancy, Sentence (1) need not apply if exits are placed along the perimeter of the floor area and are not more than 60 m apart, measured along the perimeter, provided each main aisle in the floor area leads directly to an exit.

(3)  Exits shall be located and arranged so that they are clearly visible or their locations are clearly indicated and they are accessible at all times.

3.4.2.6.  Principal Entrance

(1)  For the purposes of this Section, at least one door at every principal entrance from ground level shall be designed in accordance with the requirements for exits.

3.4.3.  Width and Height of Exits

3.4.3.1.  Exit Width Based on Occupant Load

(1)  For the purpose of determining the aggregate width of exits, the occupant load of every room or floor area shall be determined in conformance with Subsection 3.1.17.

(2)  Except as permitted by Sentence 3.4.3.2.(4), the required exit width shall be cumulative if 2 or more exits converge.

3.4.3.2.  Exit Width

(1)  Except as permitted by Sentence (3), the minimum aggregate required width of exits serving floor areas intended for assembly occupancies, residential occupancies, business and personal services occupancies, mercantile occupancies, and industrial occupancies shall be determined by multiplying the occupant load of the area served by,

(a)	6.1 mm per person for ramps with a slope of not more than 1 in 8, doorways, corridors and passageways,

(b)	8 mm per person for a stair consisting of steps whose rise is not more than 180 mm and whose run is not less than 280 mm, or

(c)	9.2 mm per person for,

(i)	ramps with a slope of more than 1 in 8, or

(ii)	stairs, other than stairs conforming to Clause (b).

(2)  The minimum aggregate width of exits serving floor areas intended for a care or detention occupancy shall be determined by multiplying the occupant load of the area served by 18.4 mm per person.

(3)  The minimum aggregate width of means of egress serving a Group A, Division 4 occupancy shall be determined by multiplying the occupant load of the area served by,

(a)	1.8 mm per person for,

(i)	aisles,

(ii)	stairs other than exit stairs, and

(iii)	ramps and passageways in vomitories and exits, and

(b)	2.4 mm per person for exit stairs.

(4)  Except as required by Sentence (5), the required exit width need not be cumulative in an exit serving 2 or more floor areas located one above the other.

(5)  The required exit width for an exit stair in an assembly hall or theatre serving more than one balcony level shall conform to the appropriate requirements for stairs serving interconnected floor spaces in Article 3.2.8.4.

(6)  If more than one exit is required, every exit shall be considered as contributing not more than one half of the required exit width.

(7)  The width of an exit shall be not less than,

(a)	1 100 mm for corridors and passageways,

(b)	1 100 mm for ramps not serving patients’ or residents’ sleeping rooms,

(c)	1 100 mm for stairs, not serving patients’ or residents’ sleeping rooms, that serve more than two storeys above the lowest exit level or more than one storey below the lowest exit level,

(d)	900 mm for stairs, not serving patients’ or residents’ sleeping rooms, that serve not more than two storeys above the lowest exit level or not more than one storey below the lowest exit level,

(e)	1650 mm for stairs and ramps serving patients’ or residents’ sleeping rooms,

(f)	1 050 mm for doorways serving patients’ or residents’ sleeping rooms, and

(g)	790 mm for doorways not serving patients’ or residents’ sleeping rooms.

3.4.3.3.  Exits from Interconnected Floor Space

(1)  Exit stairs that serve interconnected floor spaces as provided in Articles 3.2.8.3. to 3.2.8.11. shall conform to the requirements in Article 3.2.8.4. and in this Section.

3.4.3.4.  Exit Width Reduction

(1)  Except as permitted by Sentences (2) to (4), no fixture, turnstile or construction shall project into or be fixed within the required width of an exit.

(2)  Exit doors shall be hung so that, when open, they shall neither diminish nor obstruct the required width of the exit by more than 50 mm for each door leaf.

(3)  Swinging doors in their swing shall not reduce the required width of exit stairs or landings to less than 750 mm or reduce the width of an exit passageway to less than the minimum required width.

(4)  Handrails and construction below handrails are permitted to project into the required width of means of egress but the projections shall be not more than 100 mm on each side of the required width.

(5)  In an elementary or secondary school, where a stair lift is installed in an exit stair, an intermediate handrail shall be installed between the path of travel of the stair lift and the remainder of the stair to ensure that the stair lift will not reduce the required width of the exit stair.

3.4.3.5.  Headroom Clearance

(1)  Except as permitted by Sentences (2) to (4), every exit shall have a headroom clearance of not less than 2 100 mm.

(2)  The headroom clearance for stairways measured vertically above any landing or the nosing of any stair tread shall be not less than 2 050 mm.

(3)  Except as permitted by Sentence (4), the headroom clearance for doorways shall be not less than 2 030 mm.

(4)  No door closer or other device shall be installed so as to reduce the headroom clearance of a doorway to less than 1 980 mm.

3.4.4.  Fire Separation of Exits

3.4.4.1.  Fire-Resistance Rating of Exit Separations

(1)  Except as permitted by Sentences (2), (4), 3.3.5.4.(3), 3.4.4.2.(2), 3.4.4.3.(1) and 3.13.3.1.(3), every exit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than that required by Subsection 3.2.2., but not less than 45 min, for,

(a)	the floor assembly above the storey, or

(b)	the floor assembly below the storey, if there is no floor assembly above.

(2)  The fire-resistance rating of the fire separation referred to in Sentence (1) need not be more than 2 h.

(3)  If an exit stair in an assembly hall or theatre serves more than one balcony level, the exit stair shall be separated from the remainder of the building in conformance with Sentence (1).

(4)  The path of exit travel may lead from an exit door or exit enclosure through open air parking that is located below a roof or floor assembly that is part of the building served by the exit door or exit enclosure where,

(a)	the portion of the path of exit travel that leads through the open air parking is not more than 9 m in length measured from the exit door to a point at ground level at the perimeter of the building,

(b)	measures are taken to prevent vehicles intended to park in spaces adjacent to the path of exit travel from encroaching on the path of exit travel, and

(c)	an alternate means of egress not leading through the open air parking is available from the interior side of the door opening onto the path of exit travel through the open air parking area.

3.4.4.2.  Exits through Lobbies

(1)  Except as permitted by Sentence (2), no exit from a floor area above or below the first storey shall lead through a lobby.

(2)  Not more than one exit from a floor area is permitted to lead through a lobby provided,

(a)	the lobby floor is not more than 4.5 m above grade,

(b)	the path of travel through the lobby to the outdoors is not more than 15 m,

(c)	the adjacent rooms or premises having direct access to the lobby do not contain a residential occupancy or an industrial occupancy, except that dwelling units may open directly onto the lobby where,

(i)	from the interior of the exit stair that opens onto the lobby there is alternate means of egress not leading through the lobby and such means of egress is entirely within the same storey as the lobby, or

(ii)	the floor area is sprinklered,

(d)	except as required by Clause (g), the lobby is not located within an interconnected floor space other than as described in Sentence 3.2.8.2.(6),

(e)	the lobby conforms to the requirements for exits, except that,

(i)	rooms other than service rooms and storage rooms are permitted to open onto the lobby,

(ii)	the fire separation between the lobby and a room used for the sole purpose of control and supervision of the building need not have a fire-resistance rating,

(iii)	the fire separation between the lobby and adjacent occupancies that are permitted to open onto the lobby need not have a fire-resistance rating provided the lobby and adjacent occupancies are sprinklered, and

(iv)	passenger elevator entrances are permitted to open onto the lobby provided the elevator entrance doors are designed to remain closed except while loading and unloading,

(f)	a fire separation, constructed in accordance with Sentence 3.4.4.1.(1), is maintained between the lobby and any exit permitted by this Sentence to lead through the lobby, and

(g)	that if the exit serves a hotel, the lobby is not located within an interconnected floor space.

3.4.4.3.  Exterior Passageway Exceptions

(1)  The requirements of Sentences 3.4.4.1.(1) and 3.2.3.13.(1) and (3) do not apply to an exterior exit passageway provided,

(a)	not less than 50% of the exterior side is open to the outdoors, and

(b)	an exit stair is provided at each end of the passageway.

3.4.4.4.  Integrity of Exits

(1)  A fire separation that separates an exit from the remainder of the building shall have no openings except for,

(a)	standpipe and sprinkler piping,

(b)	electrical wires and cables, totally enclosed noncombustible raceways and noncombustible piping that serve only the exit,

(c)	openings required by the provisions of Subsection 3.2.6.,

(d)	exit doorways, and

(e)	wired glass and glass block permitted by Article 3.1.8.14.

(2)  Exits within scissors stairs and other contiguous exit stairways shall be separated from each other by a smoke-tight fire separation having a fire-resistance rating not less than that required for the floor assembly through which they pass.

(3)  Fire separations separating contiguous stairs described in Sentence (2) shall not be pierced by doorways, ductwork, piping or any other openings that affect the continuity of the separation.

(4)  A fuel-fired appliance shall not be installed in an exit.

(5)  An exit shall not be used as a plenum for a heating, ventilating or air-conditioning system.

(6)  An exit shall be designed for no purpose other than for exiting, except that an exit is permitted also to be designed to serve as an access to a floor area.

(7)  A service room shall not open directly into an exit.

(8)  Storage rooms, washrooms, toilet rooms, laundry rooms and similar ancillary rooms shall not open directly into an exit.

(9)  Service spaces referred to in Sentence 3.2.1.1.(9) shall not open directly into an exit.

(10)  In elementary and secondary schools, an exit shall be designed so that it does not serve as an access from one portion of a floor area to another portion of the same floor area.

3.4.5.  Exit Signs

3.4.5.1.  Exit Signage

(1)  Except as required by Sentences (7) and (9), every exit door shall have an exit sign placed over or adjacent to it if the exit serves,

(a)	a building more than 2 storeys in building height,

(b)	a building having an occupant load more than 150, or

(c)	a room or floor area that has a fire escape as part of a required means of egress.

(2)  Except as provided in Sentence (8), every exit sign shall,

(a)	be visible from the exit approach,

(b)	have the word EXIT or the words EXIT/SORTIE displayed in plain legible letters, and

(c)	be illuminated continuously while the building is occupied.

(3)  Exit signs shall consist of red letters on a contrasting background or a red background with contrasting letters, with the letters having a 19 mm stroke and a height not less than,

(a)	114 mm when internally illuminated, and

(b)	150 mm when externally illuminated.

(4)  If illumination of an exit sign is provided from an electrical circuit, that circuit shall,

(a)	serve no equipment other than emergency equipment, and

(b)	be connected to an emergency power supply as described in Sentence 3.2.7.4.(1)

(5)  If necessary, the direction of egress in public corridors and passageways shall be indicated by a sign conforming to Sentences (2) to (4) with a suitable arrow or pointer indicating the direction of egress.

(6)  Except for egress doorways described in Sentence 3.3.2.3.(4), an exit sign conforming to Sentences (2) to (4) shall be placed over or adjacent to every egress doorway from rooms with an occupant load more than 60 in Group A, Division 1 occupancies, dance halls, licensed beverage establishments and other similar occupancies that, when occupied, have lighting levels below the level that would provide easy identification of the egress doorway.

(7)  Except for suite doors opening directly to the exterior, every exit serving a hotel shall have an exit sign placed over or adjacent to it.

(8)  If an exit sign having the word EXIT is installed in conformance with this Article, an additional sign displaying the word SORTIE is permitted to be installed.

(9)  An exit sign is not required within a suite containing a Group B, Division 3 occupancy that contains sleeping accommodation for not more than 10 persons and not more than 6 occupants require assistance in evacuation in case of an emergency.

3.4.5.2.  Signs within Exit Facilities

(1)  In a building more than 2 storeys in building height, any part of an exit ramp or stair that continues up or down past the lowest exit level shall be clearly marked by a sign indicating that it does not lead to an exit.

(2)  An exit stair serving a building more than 6 storeys in building height shall be clearly marked by signs indicating that it does not lead to an exit at the roof level.

3.4.6.  Types of Exit Facilities

3.4.6.1.  Slip Resistance of Ramps and Stairs

(1)  The surfaces of ramps, landings and treads,

(a)	shall have a finish that is slip resistant, and

(b)	if accessible to the public, shall have either a colour contrast or a distinctive pattern to demarcate the leading edge of the tread and the leading edge of the landing, as well as the beginning and end of a ramp.

(2)  Treads and landings of exterior exit stairs shall be designed to be free of ice and snow accumulations if the stairs,

(a)	are more than 10 m high, or

(b)	serve a hotel.

3.4.6.2.  Minimum Number of Risers

(1)  Except as permitted by Sentence 3.3.2.13.(1), every flight of interior stairs shall have no fewer than 3 risers.

3.4.6.3.  Landings and Maximum Vertical Rise of Stair Flights

(1)  No flight of stairs shall have a vertical rise of more than 3.7 m between floors or landings, except that a flight of stairs serving as an exit in a Group B, Division 2 or 3 occupancy shall have a vertical rise not more than 2 400 mm between floors or landings.

(2)  Except as provided in Sentence (6), the length and width of a landing shall be at least the width of the stairway in which it occurs, except that in a straight run the length of the landing need not be more than 1 100 mm.

(3)  Where a doorway or stairway empties onto a ramp through a side wall, there shall be a level area extending across the full width of the ramp, and for a distance of 300 mm on either side of the wall opening, or on one side if the opening abuts on an end wall.

(4)  Where a doorway or stairway empties onto a ramp through an end wall, there shall be a level area extending across the full width of the ramp and along its length for not less than 900 mm.

(5)  A landing shall be provided at the top and bottom of every flight of stairs or section of a ramp.

(6)  Where the direction of exit travel changes at a landing, the landing is permitted to be chamfered or curved in plan, provided the required width of the stair is maintained where measured perpendicular to the direction of exit travel across the landing.

3.4.6.4.  Handrails

(1)  A ramp or stairway shall have a handrail on at least one side, and if 1 100 mm or more in width, shall have handrails on both sides.

(2)  If the required width of a ramp or flight of stairs is more than 2 200 mm, one or more intermediate handrails continuous between landings shall be provided, and located so that there will be not more than 1 650 mm between handrails.

(3)  Handrails shall be continuously graspable along their entire length and shall have,

(a)	a circular cross-section with an outside diameter not less than 30 mm and not more than 43 mm, or

(b)	any non-circular shape with a graspable portion that has a perimeter not less than 100 mm and not more than 125 mm and whose largest cross-sectional dimension is not more than 45 mm.

(4)  Handrails on stairs and ramps shall be not less than 865 mm and not more than 965 mm high, measured vertically from a line drawn through the outside edges of the stair nosing or from the surface of the ramp, except that handrails not meeting these requirements are permitted provided they are installed in addition to the required handrail.

(5)  Except as required by Sentence (11) and except where interrupted by doorways or newels at changes in direction, at least one handrail shall be continuous throughout the length of a stairway or ramp, including landings.

(6)  Handrails shall be terminated in a manner that will not obstruct pedestrian travel or create a hazard.

(7)  At least one handrail shall,

(a)	in the case of a stair,

(i)	extend horizontally at the required height, not less than 300 mm beyond the top riser, and

(ii)	continue to slope for a depth of one tread beyond the bottom riser followed by a 300 mm horizontal extension, and

(b)	in the case of a ramp, extend horizontally at the required height, not less than 300 mm beyond the top and bottom edges of the incline.

(8)  The clearance between a handrail and any surface behind it shall be not less than 50 mm.

(9)  Handrails and their supports shall be designed and constructed to withstand the loading values obtained from the nonconcurrent application of,

(a)	a concentrated load not less than 0.9 kN applied at any point and in any direction for all handrails, and

(b)	a uniform load not less than 0.7 kN/m applied in any direction to handrails not located within dwelling units.

(10)  A ramp shall have handrails on both sides.

(11)  In a nursing home, a home for the aged and a Group B, Division 3 occupancy, a continuous handrail shall be provided on both sides of a stairway throughout the length of the stairway, including landings, except where a handrail is interrupted by doorways or newels at changes in direction.

3.4.6.5.  Guards

(1)  Every exit shall have a wall or a well-secured guard on each side.

(2)  Except as required by Sentence (4), the height of guards for exit stairs shall be not less than 920 mm measured vertically to the top of the guard from a line drawn through the outside edges of the stair nosings and 1 070 mm around landings.

(3)  Exit ramps and their landings shall be protected with guards not less than 1 070 mm measured vertically to the top of the guard from the ramp surface where the difference in elevation between the adjacent ground or floor level and the ramp is more than 600 mm.

(4)  The height of guards for exterior stairs and landings more than 10 m above adjacent ground level shall be not less than 1 500 mm measured vertically to the top of the guard from the surface of the landing or a line drawn through the outside edges of the stair nosings.

(5)  Except as provided in Sentence (6), openings through any guard that is required by Sentence (1) shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard.

(6)  Openings through any guard that is required by Sentence (1) and that is installed in a building of industrial occupancy shall be of a size that will prevent the passage of a sphere having a diameter more than 200 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard.

(7)  In a stairway, a window for which the distance measured vertically between the bottom of the window and a line drawn through the outside edges of the stair nosings is less than 900 mm, or a window that extends to less than 1 070 mm above the landing, shall,

(a)	be protected by a guard that is,

(i)	located approximately 900 mm above a line drawn through the outside edges of the stair nosings, or

(ii)	not less than 1 070 mm high measured to the top of the guard from the surface of the landing, or

(b)	be fixed in position and designed to resist the lateral design loads specified for guards and walls in Articles 4.1.5.15. and 4.1.5.17.

(8)  Unless it can be shown that the location and size of openings do not present a hazard, a guard shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level being protected by the guard will facilitate climbing.

3.4.6.6.  Ramp Slope

(1)  Except as required for aisles by Article 3.3.2.4., the maximum slope of a ramp shall be,

(a)	1 in 10 in any assembly occupancy, care or detention occupancy or residential occupancy,

(b)	1 in 6 in rooms or floor areas classified as mercantile occupancy or industrial occupancy,

(c)	1 in 8 in any other floor area, and

(d)	1 in 10 for an exterior ramp.

3.4.6.7.  Treads and Risers

(1)  Except as permitted for dwelling units and by Sentence 3.4.7.5.(1) for fire escapes, steps for stairs shall have a run of not less than 255 mm and not more than 355 mm between successive steps.

(2)  Steps for stairs referred to in Sentence (1) shall have a rise between successive treads not less than 125 mm and not more than 200 mm.

(3)  Treads and risers in every exit stair, except a fire escape stair, shall have uniform run and rise in any one flight, and shall not alter significantly in run and rise in successive flights in any stair system.

(4)  Except as permitted by Sentence (6), the leading edge of a stair tread shall have either a radius or a bevel between 6 mm and 10 mm in horizontal dimension.

(5)  The front edge of stair treads in exits and public access to exits shall be at right angles to the direction of exit travel.

(6)  If resilient material is used to cover the leading edge of a stair tread, the minimum radius or bevel required by Sentence (4) is permitted to be reduced to 3 mm.

3.4.6.8.  Curved Stairs

(1)  Except as permitted by Sentence (2), tapered treads shall not be used in an exit.

(2)  A curved stair used as an exit shall have,

(a)	a handrail on each side,

(b)	treads with a minimum run of 240 mm exclusive of nosings,

(c)	treads that conform to Article 3.4.6.7. where they are measured 230 mm away from the handrail at the narrow end of the tread, and

(d)	an inside radius that is not less than twice the stair width.

3.4.6.9.  Horizontal Exits

(1)  Except in an elementary or secondary school that is subdivided by a firewall, the floor area on each side of a horizontal exit shall be sufficient to accommodate the occupants of both floor areas, allowing not less than 0.5 m2 of clear floor space per person, except that 1.5 m2 shall be provided for each person in a wheelchair and 2.5 m2 for each patient in bed.

(2)  If vestibules, enclosed balconies or bridges are used as parts of a horizontal exit, their clear width shall be not less than that of the exit doorways opening into them, except that handrails are not permitted to project into this clear width more than 100 mm.

(3)  In a horizontal exit where there is a difference in level between the connected floor areas, slopes not more than those specified for ramps in Article 3.4.6.6. are permitted to be used.

(4)  No stairs or steps shall be used at a horizontal exit.

(5)  If 2 doors are provided in a horizontal exit that comprises a part of the required number of exits from the floor areas on both sides of the exit,

(a)	the doors shall be mounted adjacent to each other with the door on the right side in the direction of travel through the horizontal exit swinging in the direction of travel through the horizontal exit, and

(b)	signs shall be provided on each side of the horizontal exit to indicate the door that swings in the direction of travel from that side.

(6)  If a horizontal exit utilizes bridges between buildings or outside balconies, the bridges or balconies shall conform to Article 3.2.3.19.

(7)  Any change in floor level from one side of a horizontal exit to the other side shall not exceed 2 000 mm.

3.4.6.10.  Doors

(1)  The distance between a stair riser and the leading edge of a door during its swing shall be not less than 300 mm.

(2)  No exit door shall open directly onto a step except that, if there is danger of blockage from ice or snow, an exit door is permitted to open onto not more than one step which shall be not more than 150 mm high.

(3)  Exit doors shall be clearly identifiable

(4)  No door leaf in an exit doorway with more than one leaf shall be less than 600 mm wide.

3.4.6.11.  Direction of Door Swing

(1)  Except as permitted by Sentences (2), (3) and Article 3.4.6.13., every exit door shall,

(a)	open in the direction of exit travel, and

(b)	swing on its vertical axis.

(2)  A door serving a single dwelling unit shall swing on its vertical axis.

(3)  Except in a high hazard industrial occupancy, an exit door need not swing in the direction of exit travel where it serves,

(a)	a room, suite or floor area having an occupant load of not more than 60 persons, or

(b)	as part of a means of egress from more than one floor area and the floor areas so served have a total occupant load of not more than 60 persons.

3.4.6.12.  Self-Closing Devices

(1)  An exit door that is normally required to be kept closed,

(a)	shall be provided with a self-closing mechanism, and

(b)	shall not be secured in an open position except as permitted by Sentence 3.1.8.12.(1).

3.4.6.13.  Sliding Doors

(1)  Except as permitted by Sentence (2) an exit door leading directly to outdoors at ground level is permitted to be a sliding door provided it is released in conformance with Sentence 3.3.1.11.(1).

(2)  An exit door serving a Group B, Division 1 occupancy, or an impeded egress zone in other occupancies, is permitted to be a sliding door that does not conform to Sentence 3.3.1.11.(1) provided it is designed to be released in conformance with Article 3.3.1.12.

3.4.6.14.  Revolving Doors

(1)  Except as permitted by Sentence (3), a revolving door, if used, shall,

(a)	be collapsible,

(b)	have hinged doors providing equivalent exiting capacity located adjacent to it,

(c)	be used as an exit from the ground floor level only,

(d)	be not less than 3 m from the foot of any stairway, and

(e)	have all glass in door leaves and enclosure panels conforming to,

(i)	CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(ii)	CAN/CGSB-12.11-M, “Wired Safety Glass”.

(2)  Except as permitted by Sentence (3), a revolving door shall not be considered to have an exiting capacity for more than 45 persons.

(3)  An electrically powered revolving door is not required to conform to Sentences (1) and (2) provided,

(a)	the door leaves will collapse and stop automatic rotation of the door system and not obstruct the doorway if a force not more than that specified in Sentence 3.4.6.15.(2) is applied at the centre of a door leaf,

(b)	the door leaves are capable of being opened from inside the building without requiring keys, special devices, or specialized knowledge of the door opening mechanism,

(c)	the allowable exiting capacity is based on the clear width of passage through the door enclosure when the doors are fully collapsed,

(d)	a permanent sign, whose centreline is between 1 000 mm and 1 500 mm above the floor, is placed on each face of each door leaf indicating the method for collapsing the door leaf in an emergency, and

(e)	glass used for door leaves and enclosure panels is safety glass conforming to,

(i)	CAN/CGSB-12.1-M, “Tempered or Laminated Safety Glass”, or

(ii)	CAN/CGSB-12.11-M, “Wired Safety Glass”.

3.4.6.15.  Door Release Hardware

(1)  Except for dwelling units, and except for devices on doors serving a contained use area or an impeded egress zone designed to be released in conformance with Article 3.3.1.12., and except as permitted by Sentence (4), locking, latching and other fastening devices on every exit door shall permit the door to be readily opened from the inside with not more than one releasing operation and without requiring keys, special devices or specialized knowledge of the door opening mechanism.

(2)  If a door is equipped with a latching mechanism, a device that will release the latch and allow the door to swing wide open when a force of not more than 90 N is applied to the device in the direction of travel to the exit shall be installed on,

(a)	every exit door from a floor area containing an assembly occupancy having an occupant load more than 100,

(b)	every door leading to an exit lobby from an exit stair shaft, and every exterior door leading from an exit stair shaft in a building having an occupant load more than 100, and

(c)	every exit door from a floor area containing a high hazard industrial occupancy.

(3)  Except as required by Sentence 3.8.3.3.(7), every exit door shall be designed and installed so that, when the latch is released, the door will open under a force of not more than 90 N, applied at the knob or other latch releasing device.

(4)  Electromagnetic locks that do not incorporate latches, pins or other similar devices to keep the door in the closed position are permitted to be installed on exit doors other than doors described in Sentence (5) provided,

(a)	the building is equipped with a fire alarm system conforming to Subsection 3.2.4.,

(b)	the locking device, and all similar devices in the access to exit leading to the exit door, are installed as ancillary devices to the fire alarm system and release immediately upon activation of,

(i)	the alarm signal where a single stage fire alarm system is installed,

(ii)	except as provided in Subclause (iii), the alert signal where a 2 stage fire alarm system is installed, or

(iii)	the alarm signal of a 2 stage fire alarm system installed in a care or detention occupancy,

(c)	the locking device releases immediately upon loss of power to the fire alarm control panel or loss of power controlling the electromagnetic locking mechanism and its associated auxiliary controls,

(d)	the locking device releases immediately upon actuation of a manually operated switch readily accessible only to authorized personnel and located near the main entrance of the building or in the central alarm and control facility of Sentence 3.2.6.12.(1),

(e)	the locking device releases immediately upon a fault being detected in the electrical circuit between the fire alarm control panel and the controller of the locking device,

(f)	the locking device releases immediately upon the operation of a manual pull station for the fire alarm system located on the wall not more than 600 mm from the door,

(g)	a legible sign having the words EMERGENCY EXIT UNLOCKED BY FIRE ALARM is permanently mounted on the door,

(h)	the lettering on the sign required in Clause (g) is at least 25 mm high with a 5 mm stroke,

(i)	upon release, the locking device must be reset manually by the actuation of the switch referred to in Clause (d),

(j)	the operation of any by-pass switch, where provided for testing of the fire alarm system, causes an audible signal and a visual signal to be indicated at the fire alarm annunciator panel and at the monitoring station of Clause 3.2.4.7.(4) (a), and

(k)	emergency lighting is provided at the doors.

(5)  Except as permitted in Sentences (6) and (7), electromagnetic locks are not permitted to be installed on exit doors,

(a)	described in Clause (2)(a), (b) or (c),

(b)	serving an elementary or secondary school, or

(c)	leading directly from a high hazard industrial occupancy.

(6)  Electromagnetic locks are permitted to be installed on an exterior door leading from an exit stairway in a building serving only a Group B, Division 2 major occupancy or a Group B, Division 3 major occupancy.

(7)  Electromagnetic locks are permitted to be installed on an exit door that serves only a gaming premises if,

(a)	the gaming premises is located within a sprinklered floor area,

(b)	smoke detectors are installed in each room and each corridor accessible to the public,

(c)	a force of not more than 90 N applied to the door opening hardware initiates an irreversible process that will release the locking device within 15 s and not relock until the door has been opened, and

(d)	a legible sign conforming with Clause (4) (h) is permanently mounted on the exit door to indicate that the locking device will release within 15 s of applying pressure to the door release hardware.

(8)  Door hardware for the operation of the doors referred to in this Section shall be installed at a height not more than 1 200 mm above the finished floor.

3.4.6.16.  Reserved

3.4.6.17.  Emergency Access to Floor Areas

(1)  In a building more than 6 storeys in building height,

(a)	except as permitted by Sentence (3), doors providing access to floor areas from exit stairs shall not have locking devices to prevent entry into,

(i)	any floor area designated as an area of refuge,

(ii)	floor areas located at intervals of 5 storeys or less, and

(iii)	at least one of the three highest storeys,

(b)	doors referred to in Clause (a) that provide access into the floor area shall be identified by a sign on the stairway side to indicate that they are openable from that side, and

(c)	a master key to fit all door locking devices that are intended to prevent entry into a floor area from an exit stair shall be provided in a designated location accessible to fire fighters, or the door shall be provided with a wired glass panel not less than 0.0645 m2 in area and located not more than 300 mm from the door opening hardware.

(2)  If access to floor areas through unlocked doors is required by Clause (1)(a) or through electromagnetically locked doors as permitted by Sentence (3), it shall be possible for a person entering the floor area to have access through unlocked doors or through electromagnetically locked doors within the floor area to at least one other exit.

(3)  Electromagnetic locking devices may be installed on the doors providing access to floor areas from exit stairs as required by Clause (1)(a), provided all locking device release and signage provisions in Sentence 3.4.6.15.(4) are installed on both sides of the doors.

(4)  In a building not more than 6 storeys in building height, doors providing access from exit stairs to a floor area containing a hotel are permitted to have locking devices to prevent entry into the floor area provided the requirements in Clause (1)(c) are complied with.

3.4.6.18.  Floor Numbering

(1)  Arabic numerals indicating the assigned floor number shall,

(a)	be mounted permanently on each side of doors to exit stair shafts,

(b)	be not less than 60 mm high, raised approximately 0.7 mm above the surface,

(c)	be located 1 500 mm from the finished floor, and

(d)	be contrasting in colour with the surface to which they are applied.

(2)  Upper case letters indicating the designation assigned to each exit stair shaft shall be mounted permanently on each side of doors to the exit stair shaft and shall,

(a)	be not less than 60 mm high, raised approximately 0.7 mm above the surface,

(b)	be located 1 500 mm from the finished floor, and

(c)	be contrasting in colour with the surface on which they are applied.

3.4.7.  Fire Escapes

3.4.7.1.  Scope

(1)  Except as permitted by Sentence (2), fire escapes shall not be erected on a building.

(2)  If it is impracticable to provide one or more of the exit facilities listed in Article 3.4.1.4., fire escapes conforming to Articles 3.4.7.2. to 3.4.7.7. are permitted to serve floor areas in an existing building provided the floor areas served are,

(a)	not in an elementary or secondary school,

(b)	not more than 2 storeys above ground level in care or detention occupancies, and

(c)	not more than 5 storeys above ground level in other occupancies.

3.4.7.2.  Fire Escape Construction

(1)  Fire escapes shall be of metal or concrete, of the stair type extending to ground level, constructed throughout in a strong substantial manner and securely fixed to the building, except that wooden fire escapes are permitted to be used on buildings of combustible construction if all posts and brackets are not less than 89 mm in their least dimension and all other woodwork is not less than 38 mm in its least dimension.

3.4.7.3.  Access to Fire Escapes

(1)  Access to fire escapes shall be from corridors through doors at floor level, except that access from a dwelling unit is permitted to be through a casement window having an unobstructed opening not less than 1 100 mm high by 550 mm wide with a sill height of not more than 900 mm above the inside floor.

(2)  The clear area of a fire escape balcony onto which a door opens, shall be not less than 1 m2.

3.4.7.4.  Protection of Fire Escapes

(1)  If a fire escape serves any storey above the second, openings located in a zone described in Sentence (2), including access doorways in the exterior walls of the building to which the fire escape is attached, shall be protected by closures conforming to Subsection 3.1.8.

(2)  The zone referred to in Sentence (1) extends from any balcony, platform or stairway of a fire escape to a distance,

(a)	3 m horizontally,

(b)	10 m below, and

(c)	1 800 mm above.

3.4.7.5.  Stairs

(1)  Stairs shall be inclined at an angle of not more than 45 with the horizontal, and their steps shall have risers not more than 210 mm high and treads not less than 220 mm wide exclusive of nosing.

(2)  Stairway headroom shall be not less than 1 950 mm plus the height of one riser measured vertically above the nosing of any tread or platform.

(3)  The width of a fire escape shall conform to Articles 3.4.3.1., 3.4.3.2. and 3.4.3.4., except that the width is permitted to be reduced to 550 mm provided the fire escape serves,

(a)	not more than 3 storeys, and

(b)	not more than 15 persons.

(4)  If a flight of stairs leading to the ground at the foot of a fire escape is not fixed in position, it shall,

(a)	be held in the raised position without a latch or locking device,

(b)	be fitted with a counterbalancing device,

(c)	be easily and quickly brought into position for use, and

(d)	reach the ground in the lowered position.

3.4.7.6.  Guards and Railings

(1)  The open sides of every platform, balcony and stairway forming part of a fire escape shall be protected by guards not less than 920 mm high measured vertically above the nosing of any tread or platform.

(2)  The top rail of a guard is permitted to serve as a handrail if it is free from obstructions that could break a handhold.

(3)  A wall handrail shall be installed if the fire escape is more than 550 mm wide.

(4)  Openings through any guard that is required by Sentence (1) shall be of a size that will prevent the passage of a sphere having a diameter more than 100 mm unless it can be shown that the location and size of openings that exceed this limit do not represent a hazard.

(5)  Unless it can be shown that the location and size of openings do not present a hazard, a guard for a fire escape shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above a platform or the nosing of any tread will facilitate climbing.

3.4.7.7.  Landings

(1)  Platforms for a fire escape shall be provided in conformance with the requirements for stair landings in Article 3.4.6.3.

Section 3.5.  Vertical Transportation

3.5.1.  General

3.5.1.1.  Scope

(1)  This Section applies to vertical transportation facilities installed in a building, including elevators, escalators and dumbwaiters.

(2)  Elevators in a building within the scope of Subsection 3.2.6. shall conform to Articles 3.2.6.8. and 3.2.6.9.

3.5.2.  Elevator Requirements

3.5.2.1.  Required Elevator

(1)  Except as provided in Sentence (2), in a Group B, Division 2 or 3 occupancy, if sleeping rooms or patient or resident services are provided on more than one floor level and the floor levels are not connected by ramps conforming to Article 3.8.3.4., such floor levels shall be served by at least one elevator that is large enough to accommodate a stretcher in a horizontal position.

(2)  Sentence (1) does not apply to those parts of a floor area classified as a Group B, Division 3 occupancy if,

(a)	those portions of the floor area contain sleeping accommodation for not more than 10 persons, and

(b)	not more than six occupants require assistance in evacuating in the case of an emergency.

3.5.2.2.  Barrier-Free Design

(1)  Passenger elevators shall conform to Appendix E of CSA B44, “Safety Code for Elevators”.

3.5.3.  Fire Separations

3.5.3.1.  Fire Separations for Elevator Hoistways

(1)  Except as permitted by Sentence (2), a vertical service space used as an elevator hoistway shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for,

(a)	the floor assembly above the storey, or

(b)	the floor assembly below the storey, if there is no floor assembly above.

(2)  Passenger elevators, other than those provided for fire fighters in accordance with Article 3.2.6.9., are permitted to be located within or adjacent to the opening of an interconnected floor space protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.11., Sentences 3.2.8.2.(4) and (6) without being enclosed in a hoistway separated from the remainder of the interconnected floor space provided the elevator machinery is located in a room separated from the remainder of the building by a fire separation whose fire-resistance rating is not less than that required for hoistways by Sentence (1).

(3)  Where the elevator described in Sentence (2) has doors opening into storeys above or below the interconnected floor space it shall be protected by vestibules conforming to the requirements of Sentence 3.2.8.5.(1).

Table 3.5.3.1.
Fire Separation for Vertical Transportation Space

Forming Part of Articles 3.5.3.1. and 3.5.3.2.

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Fire-Resistance Rating of Fire Separation Required for Floor Assembly | Minimum Fire-Resistance Rating of Vertical Service Space for Elevator Hoistway | Minimum Fire-Resistance Rating of Vertical Service Space for Dumbwaiters |
| less than 45 min | 45 min | --- |
| 45 min | 45 min | 45 min |
| 1 h | 1 h | 45 min |
| 1.5 h | 1 h | 1 h |
| 2 h or more | 1.5 h | 1 h |

3.5.3.2.  Vertical Service Spaces for Dumbwaiters

(1)  A vertical service space containing a dumbwaiter shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for,

(a)	the floor assembly above the storey, or

(b)	the floor assembly below the storey, if there is no floor assembly above.

3.5.3.3.  Fire Separations for Elevator Machine Rooms

(1)  Except as permitted by Sentence (2), a room containing elevator machinery shall be separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway.

(2)  A room containing elevator machinery need not be separated from the elevator hoistway that it serves provided the room and the hoistway are separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway.

3.5.4.  Dimensions and Signs

3.5.4.1.  Elevator Car Dimensions

(1)  If an elevator is installed to conform to the requirements of Article 3.3.1.7., or if one or more elevators are provided in a building more than three storeys in building height, each storey having elevator service shall be served by at least one elevator that has inside dimensions that will accommodate and provide adequate access for a patient stretcher 2 010 mm long and 610 mm wide in the prone position

(2)  An elevator satisfying the requirements of Sentence (1) shall be clearly identified on the main entrance level of the building.

Section 3.6.  Service Facilities

3.6.1.  General

3.6.1.1.  Scope

(1)  The provisions of this Section apply to horizontal service spaces, vertical service spaces, attic or roof spaces, ducts, crawl spaces, shaft spaces, service rooms, and mechanical penthouses, and facilities contained in any of them.

(2)  Except for plenum requirements in 3.6.4.3., the fire safety characteristics of heating, ventilating and air-conditioning systems shall comply with Part 6.

3.6.1.2.  Reserved

3.6.1.3.  Storage Use Prohibition

(1)  Service spaces shall not be designed to facilitate subsequent use as storage space.

3.6.1.4.  Reserved

3.6.1.5.  Fixed Access Ladders

(1)  If a fixed ladder is installed to provide access to a roof of a building, the design and installation of the attachment and anchorage system for the ladder shall be as described in Supplementary Standard SB-8.

3.6.2.  Service Rooms

3.6.2.1.  Fire Separations around Service Rooms

(1)  Except as permitted by Sentences (2), (8), (9) and (10), fuel-fired appliances shall be installed in service rooms separated from the remainder of the building by fire separations having a fire-resistance rating not less than 1 h.

(2)  Except as required by Sentence (3), a fuel-fired appliance that serves only one room or suite is not required to be installed in a service room separated from the remainder of the building.

(3)  A solid fuel fired appliance shall not be located in a repair garage, a storage garage, or any other location where it could be exposed to flammable vapours or gases unless,

(a)	it is enclosed in a service room that is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h,

(b)	it is supplied with combustion air directly from outside the building, and

(c)	the heat that it generates is supplied indirectly to the space served by means of ducts or piping.

(4)  A service room containing an incinerator shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h.

(5)  Equipment that uses a liquid having a flash point below 93.3°C shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(6)  Electrical equipment that is required to be located in a service room by a regulation made under the Electricity Act, 1998, shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(7)  Except as permitted by Sentence (8), in a storey that is not sprinklered, a service room that contains service equipment other than that addressed by Sentences (1) to (6), shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

(8)  If a service room referred to in Sentence (7) contains a limited quantity of service equipment, and the service equipment neither constitutes a fire hazard nor is essential to the operation of fire safety systems in the building, the requirements for a fire separation shall not apply.

(9)  A fire separation is not required between a fireplace and the space it serves.

(10)  A fire separation is not required between a roof-top appliance and the building it serves.

(11)  The fire separation provisions for a fuel-fired appliance in a portable classroom shall conform to Article 3.9.3.7.

3.6.2.2.  Service Rooms under Exits

(1)  A service room containing service equipment subject to possible explosion, such as boilers operating in excess of 100 kPa (gauge) and some types of refrigerating machinery and transformers, shall not be located directly under a required exit.

3.6.2.3.  Service Equipment

(1)  A service room containing space heating, space cooling and service water heating appliances is permitted to contain other service equipment such as electrical service equipment.

3.6.2.4.  Incinerator Rooms

(1)  A service room containing an incinerator shall not contain other fuel-fired appliances.

3.6.2.5.  Combustible Refuse Storage

(1)  Except as required by Sentence 3.6.3.3.(9), a room for the storage of combustible refuse shall be,

(a)	separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h, and

(b)	sprinklered.

3.6.2.6.  Door Swing for Service Rooms

(1)  A swing-type door from a service room containing a boiler or incinerator shall swing outward from the room, except that the door shall swing inward if the door opens onto a corridor or any room used for an assembly occupancy.

3.6.2.7.  Electrical Equipment Vaults

(1)  Where an electrical equipment vault is required by a regulation made under the Electricity Act, 1998, the electrical equipment vault shall be totally enclosed by a fire separation of solid masonry or concrete construction having a fire-resistance rating of not less than 3 h if the vault is not provided with an automatic fire extinguishing system and not less than 2 h if the vault is so protected.

(2)  Where a building is required to be sprinklered, the electrical equipment vault described in Sentence (1) need not be sprinklered provided,

(a)	the vault is designed for no purpose other than to contain the electrical equipment, and

(b)	a smoke detector is provided in the vault that will actuate the building fire alarm system in the event of a fire in the vault.

(3)  A vault, that is part of a building and houses electrical equipment indoors, shall have,

(a)	roofs or ceilings consisting of reinforced concrete of adequate strength for the conditions and not less than 150 mm thick, and

(b)	floors consisting of reinforced concrete of adequate strength for the conditions and not less than 150 mm thick, except that floors that are at excavation level are permitted to be of reinforced concrete not less than 100 mm thick.

(4)  Walls, roofs or ceilings, and floors shall be adequately anchored together in a manner designed to resist dislodgement by explosion.

(5)  Only pipes or ducts necessary for fire protection or the proper operation of the electrical installation shall penetrate the fire separations surrounding the electrical equipment vault.

(6)  A ventilation duct or opening, that penetrates the fire separation to the outdoors, need not be protected by a closure at the penetration.

(7)  Each door to an electrical equipment vault shall be provided with a substantial lock or padlock.

(8)  Explosion-relief devices and vents or other protective measures shall be provided for every electrical equipment vault containing dielectric liquid filled electrical equipment in conformance with Sentence 3.3.1.19.(2).

(9)  Every electrical equipment vault shall be provided with a ventilation system designed in conformance with Part 6 to prevent the ambient temperature in the vault from exceeding 40°C.

(10)  Where the vault ventilation system in Sentence (9) is directly from an outdoor area by natural ventilation without the use of ducts, and where the electrical equipment is the principal source of heat, the combined net area of inlet and outlet openings shall be not less than 0.002 m2/kVa of electrical equipment capacity with a minimum of 0.093 m2, except that,

(a)	where equipment in the power class as described in CAN3-C88, “Power Transformers and Reactors” is installed, ventilation requirements are permitted to be based on the actual full-load losses, or

(b)	where the equipment is installed for emergency purposes only and is not normally energized, it need not be considered in determining the ventilation requirements.

(11)  In the vault ventilation system in Sentence (10), the inlet for fresh air shall lead from an outdoor area and shall terminate at a point not more than 1 000 mm above the floor level of the vault.

(12)  Where the vault ventilation system in Sentence (9) is a mechanical system, it shall be separate from the system for the remainder of the building and shall be designed so that,

(a)	the vault temperature is thermostatically controlled,

(b)	the fan is located so that it may be serviced without danger to personnel,

(c)	a high temperature alarm is provided in the vault,

(d)	the system is automatically shut off in the event of a fire in the vault, and

(e)	a filter is provided in the air inlet if there is a possibility of dirt being drawn in.

(13)  All ventilation openings shall be protected in conformance with Sentences 6.2.3.12.(3) and (4) and the protection shall be installed in such a manner that it cannot be removed from the outside by the use of common tools and it is tamperproof.

(14)  Except as permitted in Sentence (15), the floor of the electrical equipment vault described in Sentences (1) and (2) shall be liquid tight and surrounded by liquid tight walls and sills of sufficient height to confine within the vault all of the liquid from the largest item of electrical equipment, but to a height of not less than 100 mm.

(15)  The floor of the electrical equipment vault described in Sentences (1) and (2) may be provided with a floor drain connected to a covered sump capable of holding all of the liquid from the largest item of electrical equipment, and the connection shall have a noncombustible trap to prevent the spread of fire from the vault to the sump.

3.6.2.8.  Emergency Power Installations

(1)  A generator to supply emergency power for lighting, fire safety and life safety systems shall be located in a room that,

(a)	is separated from the remainder of the building by a fire separation with a fire-resistance rating not less than ,

(i)	2 h for buildings within the scope of Subsection 3.2.6., and

(ii)	1h for other buildings, and

(b)	contains only the generating set and equipment that is related to the emergency power supply system.

3.6.2.9.  Storage of Oxygen Containers

(1)  In a Group B, Division 2 or 3 occupancy, a room for the storage of oxygen containers shall be,

(a)	separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h,

(b)	designed for the storage of oxygen containers only,

(c)	vapour tight,

(d)	lined with noncombustible finish,

(e)	separately exhausted to the exterior, and

(f)	equipped with racks to store the containers.

3.6.3.  Vertical Service Spaces and Service Facilities

3.6.3.1.  Fire Separations for Vertical Service Spaces

(1)  Except as required by Section 3.5., a vertical service space shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.6.3.1. for the fire-resistance rating required by Subsection 3.2.2. for,

(a)	the floor assembly above the storey, or

(b)	the floor assembly below the storey, if there is no floor assembly above.

(2)  A vertical service space that does not extend through the roof of a building shall be enclosed at the top with construction having a fire-resistance rating not less than that required for the vertical service space walls.

(3)  A vertical service space that does not extend to the bottom of a building shall be enclosed at the lowest level with construction having a fire-resistance rating not less than that required for the vertical service space walls.

(4)  A vent from a vertical service space not extending to the roof shall be enclosed within the building with construction having a fire-resistance rating not less than that required for the vertical service space walls.

Table 3.6.3.1.
Fire Separations for Vertical Service Space

Forming Part of Sentence 3.6.3.1.(1)

| Column 1 | Column 2 |
| --- | --- |
| Fire-Resistance Rating of Fire Separation Required for Floor Assembly | Minimum Fire-Resistance Rating of Vertical Service Space |
| less than 45 min | --- |
| 45 min | 45 min |
| 1 h | 45 min |
| 1.5 h | 1 h |
| 2 h or more | 1 h |

(5)  Only openings that are necessary for the use of the vertical service space shall be permitted through a vertical service space enclosure.

3.6.3.2.  Foamed Plastic Protection

(1)  Foamed plastic insulation in a vertical service space shall be protected in conformance with Article 3.1.5.12.

3.6.3.3.  Linen and Refuse Chutes

(1)  A linen chute or refuse chute shall,

(a)	be impervious to moisture,

(b)	have a smooth internal surface,

(c)	be corrosion-resistant,

(d)	be constructed of noncombustible material, and

(e)	be located in a shaft in which there are no services other than noncombustible drain, waste and vent piping or noncombustible water piping.

(2)  A shaft containing a linen chute or refuse chute shall have a fire-resistance rating conforming to Sentence 3.6.3.1.(1), but not less than,

(a)	1 h if the chute outlet for the discharge room is protected by an automatic, self-latching closure held open by a fusible link, or

(b)	2 h if no closure is provided at the chute outlet into the discharge room.

(3)  An interior linen chute or refuse chute shall extend not less than 1 000 mm above the roof and shall be vented above the roof with a vent that,

(a)	has an unobstructed area not less than the cross-sectional area of the chute, and

(b)	is equipped with a cover that will open automatically, or that can be opened manually, in the event of a fire in the chute.

(4)  Intake openings for a linen chute or a refuse chute shall,

(a)	have an area not more than 60% of the cross-sectional area of the chute, and

(b)	be fitted with closures designed to close automatically and latch after use.

(5)  Intake openings for a linen chute or a refuse chute shall be located in rooms or compartments that,

(a)	have no dimension less than 750 mm,

(b)	are separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 45 min,

(c)	are designed for no other purpose, and

(d)	do not open directly into an exit.

(6)  Sprinklers shall be installed at the top of each linen chute or refuse chute, at alternate floor levels and in the room or bin into which the chute discharges.

(7)  The room into which a linen chute discharges shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h.

(8)  A refuse chute shall be equipped at the top with spray equipment for washing-down purposes.

(9)  A refuse chute shall discharge only into a room or bin separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h.

(10)  The room or bin into which a refuse chute discharges shall be of sufficient size to contain the refuse between normal intervals of emptying, be impervious to moisture and be equipped with a water connection and floor drain for washing-down purposes.

(11)  A room into which a refuse chute discharges shall contain no service equipment that is not related to refuse handling and disposal.

3.6.3.4.  Exhaust Duct Negative Pressure

(1)  If a vertical service space contains an exhaust duct that serves more than one fire compartment, the duct shall have a fan located at or near the exhaust outlet to ensure that the duct is under negative pressure.

3.6.4.  Horizontal Service Spaces and Service Facilities

3.6.4.1.  Scope

(1)  This Subsection applies to horizontal service spaces and service facilities, including ceiling spaces, duct spaces, crawl spaces and attic or roof spaces.

3.6.4.2.  Fire Separations for Horizontal Service Spaces

(1)  A horizontal service space that penetrates a required vertical fire separation shall be separated from the remainder of the building it serves in conformance with Sentence (2).

(2)  If a horizontal service space or other concealed space is located above a required vertical fire separation other than a vertical shaft, this space need not be divided at the fire separation as required by Article 3.1.8.3. provided the construction between this space and the space below is a fire separation with a fire-resistance rating equivalent to that required for the vertical fire separation, except that the fire-resistance rating is permitted to be not less than 30 min if the vertical fire separation is not required to have a fire-resistance rating more than 45 min.

3.6.4.3.  Plenum Requirements

(1)  A concealed space used as a plenum within a floor assembly or within a roof assembly need not conform to Sentence 3.1.5.15.(1) and Article 6.2.3.2. provided,

(a)	all materials within the concealed space have a flame-spread rating not more than 25 and a smoke developed classification not more than 50, except for,

(i)	tubing for pneumatic controls,

(ii)	optical fibre cables and electrical wires and cables that exhibit a flame spread not more than 1.5 m, a smoke density not more than 0.5 at peak optical density and a smoke density not more than 0.15 at average optical density when tested in conformance with the Flame and Smoke Test in the Appendix to CAN/CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT6 Rating),

(iii)	optical fibre cables and electrical wires and cables that are located in totally enclosed noncombustible raceways,

(iv)	totally enclosed nonmetallic raceways that exhibit a horizontal flame distance of not more than 1.5 m, an average optical smoke density of not more than 0.15, and a peak optical smoke density of not more than 0.5 when tested in conformance with the Test for Flame Propagation and Smoke Density Values in Section 3.3 of the ULC/ORD-C2024, “Fire Tests for Optical Fibre Cable Raceway” (FT-6 Rating), and

(v)	single conductor electrical wires and cables that exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test —Cables in Cabletrough in Clause 4.11.4. of CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables” (FT4 Rating), and

(b)	the supports for the ceiling membrane are of noncombustible material having a melting point not below 760°C.

(2)  If a concealed space referred to in Sentence (1) is used as a return-air plenum and incorporates a ceiling membrane that forms part of the required fire-resistance rating of the assembly, every opening through the membrane shall be protected by a fire stop flap that shall,

(a)	stop the flow of air into the concealed space in the event of a fire,

(b)	be supported in a manner that will maintain the integrity of the ceiling membrane for the duration of time required to provide the required fire-resistance rating, and

(c)	conform to CAN4-S112.2-M, “Fire Test of Ceiling Firestop Flap Assemblies”.

(3)  Asbestos paper shall not be exposed in supply and return-air systems.

3.6.4.4.  Attic or Roof Space Access

(1)  An attic or roof space more than 600 mm high shall be provided with access from the floor immediately below by a hatchway not less than 550 mm by 900 mm or by a stairway.

3.6.4.5.  Horizontal Service Space Access

(1)  A horizontal service space, consisting of ceiling and duct spaces, that is more than 1 200 mm high and 600 mm wide shall have inspection doors not less than 300 mm in both horizontal and vertical dimensions placed so that the entire interior of the duct or space can be viewed.

3.6.4.6.  Crawl Space Access

(1)  A crawl space shall have at least one access opening not less than 550 mm by 900 mm.

Section 3.7.  Health Requirements

3.7.1.  Height and Area of Rooms

3.7.1.1.  Room and Space Height

(1)  The height of every room and space shall be sufficient so that the ceiling or ceiling fixtures do not obstruct movement or activities below.

(2)  The unobstructed height in dwelling units and sleeping rooms in Group C occupancies shall conform to Subsection 9.5.3.

3.7.1.2.  Residential Room Dimensions

(1)  The areas of rooms in dwelling units, dormitories, boarding houses and rooming houses shall conform to Part 9.

3.7.1.3.  Sleeping Areas in Group B and Child Care Facilities

(1)  Except as provided in Sentence (2), a sleeping area in a Group B occupancy shall provide not less than 4.7 m2 per person in a room having,

(a)	an area not less than 7 m2,

(b)	a horizontal dimension not less than 2 000 mm, and

(c)	a ceiling height not less than 2 300 mm.

(2)  Sleeping rooms for residents in nursing homes shall have, exclusive of space provided for washrooms and for built-in or portable clothes closets, a floor space not less than,

(a)	10.22 m2 in a single-bed unit,

(b)	16.72 m2 in a two-bed unit,

(c)	25.08 m2 in a three-bed unit, and

(d)	29.73 m2 in a four-bed unit.

(3)  A child care facility shall provide sleeping accommodation having not less than 0.93 m2 of floor surface area for each child with not less than 2 300 mm ceiling height over the entire room area.

3.7.1.4.  Sleeping Areas in Camps

(1)  Recreational camps shall have an area in the sleeping quarters of not less than 3.72 m2 per camper or, if double or triple tier bunk units are used, 2.79 m2 per camper.

(2)  A camp for housing of workers shall have an area of not less than 3.72 m2 per employee in every room used for sleeping purposes.

3.7.2.  Windows

3.7.2.1.  Window Areas

(1)  Except as provided in Sentences (2) and (3) or otherwise permitted, every room used for sleeping in any building, and every principal room such as living room, dining room or combination of them in dwelling units shall be provided with windows having areas conforming to Part 9, except that Article 9.7.1.3 does not apply.

(2)  Nursing homes shall have,

(a)	in an activity room, a sitting room or a lounge, one or more windows with a total unobstructed glass area, exclusive of skylights, of not less than 10% of the area of the room, and

(b)	in a residents’ sleeping room, one or more windows that,

(i)	have a total unobstructed glass area, exclusive of skylights, of not less than 10% of the area of the room,

(ii)	open to the outdoors and have a total unobstructed glass area, exclusive of skylights, of not less than 5% of the area of the room, and

(iii)	are installed with the bottom edge of the glass of every window not more than 660 mm above the floor.

(3)  Play activity rooms in a child care facility and work areas in live/work units shall have one or more windows that conform to Clause (2)(a).

3.7.2.2.  Window Protection in Apartment Buildings

(1)  In Group C major occupancy apartment buildings protection shall be provided at windows to minimize the hazards to children in accordance with Sentences (2) to (4).

(2)  Fixed windows within dwelling units that extend to less than 1 000 mm from the floor shall be protected by guards to at least 1 000 mm above the floor, or shall be designed to withstand the lateral design loads for balcony guards in Part 4.

(3)  Except as provided in Sentence (4), in dwelling units any window located more than 2 000 mm above grade that opens within 1 500 mm of the floor shall be protected,

(a)	by a guard conforming to Sentence 3.3.1.17.(2),

(b)	by,

(i)	a controlled sash operation to restrict, when engaged, the opening of the operable sash to not more than 100 mm, and

(ii)	a heavy duty screen conforming to CAN/CSA-A440, “Windows”, or

(c)	by an alternative device that does not reduce the degree of safety provided by Clause (a) or (b).

(4)  Protection of a window need not be provided in a dwelling unit where an exterior balcony is constructed for the full length of a window.

3.7.3.  Reserved

3.7.4.  Plumbing Facilities

3.7.4.1.  Plumbing and Drainage Systems

(1)  Except as permitted in Sentence (3), each building situated on property that abuts on a street in which a public or municipal water main is located shall be provided with or have accessible to its occupants a plumbing system including a potable water supply, a sanitary drainage system and plumbing fixtures.

(2)  When the installation of a sanitary drainage system is not possible because of the absence of a water supply, sanitary privies, chemical closets or other means for the disposal of human waste shall be provided.

(3)  Plumbing fixtures need not be provided in a building that is not normally occupied by persons where such installations are impractical and other fixtures are available in nearby buildings when the subject building is in use.

3.7.4.2.  Plumbing Fixtures, General

(1)  For the purposes of this Subsection, the occupant load shall be determined in accordance with the provisions in Subsection 3.1.17. except that in a Group D occupancy, the area per person shall be 14 m2.

(2)  Except as provided in this Subsection, water closets shall be provided for each sex assuming that the occupant load is equally divided between males and females, unless the proportion of each sex expected in the building can be determined with reasonable accuracy.

(3)  Except as provided in Sentence (4), urinals are permitted to be substituted for water closets required by this Subsection for males and may be counted as water closets provided the number of urinals is not more than,

(a)	one fifth of the required number of water closets in hospitals and nursing homes, and

(b)	two thirds of the required number of water closets in any other occupancy.

(4)  If only 2 water closets are required for males, one urinal is permitted to be substituted for one of the water closets.

(5)  Except as required in this Subsection, at least one lavatory shall be provided in a room containing one or 2 water closets or urinals, and at least one additional lavatory shall be provided for each additional 2 water closets or urinals.

(6)  Wash fountains in circular or straight trough form are permitted to be provided in lieu of required lavatories provided each 500 mm of circumference or trough length is considered to be the equivalent of one lavatory.

(7)  The water closet and lavatory provided in the universal toilet room described in Sentence 3.8.3.12.(1) may be counted as part of the plumbing fixtures required for males and females in this Subsection if,

(a)	more than one water closet is required for males, and

(b)	more than one water closet is required for females.

(8)  Both sexes are permitted to be served by a single water closet if the occupant load is not more than 10 persons in an assembly occupancy referred to in Article 3.7.4.3. except for,

(a)	elementary and secondary schools,

(b)	child care facilities,

(c)	places of worship,

(d)	undertaking premises, and

(e)	dining rooms, restaurants, cafeterias and alcoholic beverage establishments.

(9)  Any shelf or projection above a lavatory shall be located so that it will not be a hazard.

(10)  Except for dwelling units, lavatories required by Sentence (5) shall be equipped with faucets that,

(a)	operate automatically, or

(b)	have lever type handles that do not close under spring action.

3.7.4.3.  Plumbing Fixtures for Assembly Occupancies

(1)  Except as permitted by Sentences (2) to (16) and Sentence 3.7.4.2.(8), the number of water closets required for assembly occupancies shall conform to Table 3.7.4.3.A.

Table 3.7.4.3.A.
Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(1)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Males | Minimum Number of Water Closets for Females |
| 1 - 25 | 1 | 1 |
| 26 - 50 | 1 | 2 |
| 51 - 75 | 2 | 3 |
| 76 - 100 | 2 | 4 |
| 101 - 125 | 3 | 5 |
| 126 - 150 | 3 | 6 |
| 151 - 175 | 4 | 7 |
| 176 - 200 | 4 | 8 |
| 201 - 250 | 5 | 9 |
| 251 - 300 | 5 | 10 |
| 301 - 350 | 6 | 11 |
| 351 - 400 | 6 | 12 |
| Over 400 | 7 plus 1 for each additional increment of 200 males in excess of 400 | 13 plus 1 for each additional increment of 100 females in excess of 400 |

(2)  Except for motion picture theatres, the number of water closets required for Group A, Division 1 occupancies shall conform to Table 3.7.4.3.B.

Table 3.7.4.3.B.
Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(2)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Males | Minimum Number of Water Closets for Females |
| 1 to 50 | 1 | 2 |
| 51 to 75 | 2 | 3 |
| 76 to 100 | 2 | 4 |
| 101 to 125 | 3 | 5 |
| 126 to 150 | 3 | 6 |
| 151 to 175 | 4 | 7 |
| 176 to 200 | 4 | 8 |
| 201 to 250 | 5 | 9 |
| 251 to 300 | 5 | 10 |
| 301 to 350 | 6 | 11 |
| 351 to 400 | 6 | 12 |
| over 400 | 7 plus 1 for each additional increment of 200 males in excess of 400 | 13 plus 1 for each additional increment of 100 females in excess of 400 |

(3)  The number of water closets required shall conform to Table 3.7.4.3.C. for,

(a)	motion picture theatres,

(b)	Group A, Division 3 occupancies,

(c)	Group A, Division 4 occupancies, and

(d)	outdoor pools.

Table 3.7.4.3.C.
Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(3)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| 1 to 50 | 1 |
| 51 to 150 | 2 |
| 151 to 250 | 3 |
| 251 to 375 | 4 |
| 376 to 500 | 5 |
| over 500 | 6 plus 1 for each additional increment of 150 persons of each sex in excess of 500 |

(4)  Except as provided in Sentences (6) and (7), the number of water closets required for dining rooms, restaurants and cafeteria shall conform to Table 3.7.4.3.D.

Table 3.7.4.3.D.
Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(4) and (7)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| 1 to 20 | 1 |
| 21 to 70 | 2 |
| 71 to 105 | 3 |
| 106 to 135 | 4 |
| 136 to 165 | 5 |
| 166 to 195 | 6 |
| 196 to 225 | 7 |
| 226 to 275 | 8 |
| 276 to 325 | 9 |
| 326 to 375 | 10 |
| 376 to 425 | 11 |
| over 425 | 12 plus 1 for each additional increment of 50 persons of each sex in excess of 425 |

(5)  The number of water closets required for establishments used primarily for the consumption of alcoholic beverages that provide limited or no food service shall conform to Table 3.7.4.3.E.

Table 3.7.4.3.E.
Water Closets for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(5)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| 1 to 50 | 2 |
| 51 to 70 | 3 |
| 71 to 90 | 4 |
| 91 to 110 | 5 |
| 111 to 140 | 6 |
| 141 to 180 | 7 |
| 181 to 220 | 8 |
| 221 to 260 | 9 |
| over 260 | 10 plus 1 for each additional increment of 40 persons of each sex in excess of 260 |

(6)  In every dining room, restaurant, cafeteria and alcoholic beverage establishment having more than 40 seats, separate sanitary facilities shall be provided for employees, in addition to facilities provided for patrons, and the number of water closets and lavatories required shall conform to Table 3.7.4.3.F.

Table 3.7.4.3.F.
Plumbing Fixtures for Assembly Occupancies

Forming Part of Sentence 3.7.4.3.(6) and (7)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Number of Employees of Each Sex | Minimum Number of Water Closets and Lavatories for Males | Minimum Number of Water Closets and Lavatories for Females |
| 1 to 9 | 1 | 1 |
| 10 to 24 | 2 | 2 |
| 25 to 49 | 3 | 3 |
| 50 to 74 | 4 | 4 |
| 75 to 100 | 5 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 male employees in excess of 100 | 6 plus 1 for each additional increment of 30 female employees in excess of 100 |

(7)  Except as provided in Sentence (8), in every dining room, restaurant, cafeteria and alcoholic beverage establishment having not more than 40 seats, patrons are permitted to share the sanitary facilities provided for employees, and the minimum number of water closets and lavatories shall conform to Table 3.7.4.3.D. based on,

(a)	a male occupant load of 50% of the number of seats plus the number of male employees, and

(b)	a female occupant load of 50% of the number of seats plus the number of female employees.

(8)  Where a separate employee washroom is provided, the same room may be used by both female and male employees provided that,

(a)	the total number of employees is not more than 5, and

(b)	the door to the room can be locked from the inside.

(9)  The number of employees in Sentences (6), to (8) shall be the maximum number of employees who are normally present on the premises at one time and shall include only those who are present for more than 25 per cent of the working day.

(10)  For a parking lot that is part of a restaurant where patrons are intended to eat in vehicles parked on the lot, the number of water closets required shall conform to,

(a)	Table 3.7.4.3.G. where food service by employees is not provided on the parking lot, or

(b)	Table 3.7.4.3.H. where employees serve food on the parking lot.

Table 3.7.4.3.G.
Water Closets for Assembly Occupancies

Forming part of Sentence 3.7.4.3.(10)

| Column 1 | Column 2 |
| --- | --- |
| Number of Parking Spaces | Minimum Number of Water Closets for Each Sex |
| 1 to 20 | 1 |
| 21 to 70 | 2 |
| 71 to 105 | 3 |
| 106 to 135 | 4 |
| 136 to 165 | 5 |
| 166 to 195 | 6 |
| 196 to 225 | 7 |
| 226 to 275 | 8 |
| 276 to 325 | 9 |
| 326 to 375 | 10 |
| 376 to 425 | 11 |
| over 425 | 12 plus 1 for each additional increment of 50 parking spaces in excess of 425 |

(11)  The number of water closets required for drive-in theatres shall conform to Table 3.7.4.3.H.

(12)  The number of water closets required for dance halls and recreational establishments shall be at least one fixture for each 100 males and one fixture for each 75 females.

Table 3.7.4.3.H.
Water Closets for Assembly Occupancies

Forming part of Sentences 3.7.4.3.(10) and (11)

| Column 1 | Column 2 |
| --- | --- |
| Number of Parking Spaces | Minimum Number of Water Closets for Each Sex |
| 1 to 40 | 1 |
| 41 to 140 | 2 |
| 141 to 210 | 3 |
| 211 to 270 | 4 |
| 271 to 330 | 5 |
| 331 to 390 | 6 |
| 391 to 450 | 7 |
| 451 to 550 | 8 |
| 551 to 650 | 9 |
| 651 to 750 | 10 |
| 751 to 850 | 11 |
| over 850 | 12 plus 1 for each additional increment of 100 parking spaces in excess of 850 |

(13)  In a child care facility the maximum number of children per water closet and lavatory shall conform to Table 3.7.4.3.I.

Table 3.7.4.3.I.
Plumbing Fixtures for a Child Care Facility

Forming Part of Sentence 3.7.4.3.(13)

| Column 1 | Column 2 |
| --- | --- |
| Age of Children | Maximum Number of Children per Water Closet and Lavatory |
| under 2 | 10 without regard to number of each sex |
| 2 to 5 | 10 without regard to number of each sex |
| 6 to 9 | 15 for males; 15 for females |
| over 9 | 30 for males; 26 for females |

(14)  The number of water closets required for elementary and secondary schools shall be at least one fixture for each 30 males and one fixture for each 26 females.

(15)  The number of water closets required for non-residential college buildings shall be at least one fixture for each 100 males and one fixture for each 75 females.

(16)  The number of water closets required for places of worship and undertaking premises shall be at least one fixture for each 150 persons of each sex.

3.7.4.4.  Plumbing Fixtures for Care or Detention Occupancies

(1)  The number of water closets and lavatories required for Group B, Division 1 occupancies shall be determined on the basis of the special needs of these occupancies.

(2)  In a Group B, Division 2 or 3 occupancy, washrooms shall be provided so that each washroom,

(a)	serves not more than four patients or residents,

(b)	is accessible from patients’ or residents’ sleeping rooms,

(c)	contains one water closet, and

(d)	contains one lavatory.

(3)  The number of water closets required for employees in Group B, Division 2 or 3 occupancies shall conform to Table 3.7.4.4.

Table 3.7.4.4.
Water Closets in Group B, Division 2 or 3 Occupancies

Forming Part of Sentence 3.7.4.4.(3)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |

3.7.4.5.  Plumbing Facilities for Dwelling Units

(1)  A kitchen sink, lavatory, water closet and bathtub or shower stall shall be provided for every dwelling unit where a piped water supply is available.

3.7.4.6.  Plumbing Fixtures for Other Residential Occupancies

(1)  Except for dwelling units and as provided in Sentence (2), the number of water closets required for residential occupancies shall conform to Table 3.7.4.6.

Table 3.7.4.6.
Water Closets For Residential Occupancies

Forming Part of Sentence 3.7.4.6.(1)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |

(2)  At least one water closet or privy shall be provided for every,

(a)	10 campers of each sex in a recreational camp, and

(b)	10 employees of each sex in a camp for housing of workers.

(3)  In recreational camps and camps for housing of workers, no fewer than two lavatories or provision for a pail or other portable container of sound construction shall be provided for each of the water closets or privies required in Sentence (2).

(4)  A camp for housing of workers shall include,

(a)	at least one shower or other area of bathing, and

(b)	provisions for at least one washing machine or laundry tub for every 15 beds.

3.7.4.7.  Plumbing Fixtures for Business and Personal Services Occupancies

(1)  Except as provided in Sentence (2), the number of water closets required for business and personal services occupancies shall conform to Table 3.7.4.7.

(2)  Not more than one water closet to serve both sexes need be provided in a Group D occupancy having an occupant load of not more than 10 persons.

Table 3.7.4.7.
Water Closets for Business and Personal Services Occupancies

Forming Part of Sentence 3.7.4.7.(1)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |

3.7.4.8.  Plumbing Fixtures for Mercantile Occupancies

(1)  Except as provided in this Article, the number of water closets required for employees in mercantile occupancies shall conform to Table 3.7.4.8.

Table 3.7.4.8.
Water Closets for Mercantile Occupancies

Forming Part of Sentence 3.7.4.8.(1)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |

(2)  Except as provided in Sentence (4), the number of water closets required for the public in mercantile occupancies shall be at least one fixture for each 300 males and one fixture for each 150 females, except that,

(a)	water closets provided for employees are permitted to be counted as part of those required for the public when these water closets are made accessible to the public, and

(b)	where the total area of the mercantile occupancy, excluding basements, is not more than 600 m2, not more than one water closet for each sex need be provided.

(3)  Not more than one water closet to serve both sexes need be provided in a Group E occupancy where,

(a)	the occupant load is not more than 9 persons, or

(b)	where the total area of the occupancy, excluding basements, is not more than 300 m2.

(4)  For a restaurant classified as mercantile occupancy, the number of water closets and lavatories required shall conform to Article 3.7.4.3.

3.7.4.9.  Plumbing Fixtures for Industrial Occupancies

(1)  Except as provided in Sentence (2), the number of water closets and lavatories required for industrial occupancies shall conform to Table 3.7.4.9.

Table 3.7.4.9.
Plumbing Fixtures for Industrial Occupancies

Forming Part of Sentence 3.7.4.9.(1)

| Column 1 | Column 2 |
| --- | --- |
| Number of Persons of Each Sex | Minimum Number of Water Closets and Lavatories for Each Sex |
| up to 9 | 1 |
| 10 to 24 | 2 |
| 25 to 49 | 3 |
| 50 to 74 | 4 |
| 75 to 100 | 5 |
| over 100 | 6 plus 1 for each additional increment of 30 persons of each sex in excess of 100 |

(2)  Not more than one water closet to serve both sexes need be provided in a Group F occupancy where,

(a)	the occupant load is not more than 10 persons, or

(b)	the total area of the occupancy, excluding basements, is not more than 300 m2.

3.7.4.10.  Plumbing Fixtures for Mobile Home Facilities

(1)  If mobile homes do not have individual plumbing facilities connected to a central water supply and drainage system, a service building shall be provided for public use.

(2)  The service building required by Sentence (1) shall contain,

(a)	at least one water closet for each sex if the service building facilities serve not more than 10 mobile homes, and

(b)	an additional water closet for each sex for each additional 10 mobile homes.

(3)  If a service building is required by Sentence (1) it shall contain lavatories as required by Sentence 3.7.4.2.(5) and at least,

(a)	one laundry tray or similar facility, and

(b)	one bathtub or shower for each sex.

3.7.4.11.  Safety Glass

(1)  Glass, other than safety glass, shall not be used for a shower or bathtub enclosure.

3.7.4.12.  Surface Protection

(1)  Wall and floor surfaces below the uppermost surfaces of urinals shall be protected from deterioration by impervious and durable material for a distance from the urinal to a point not less than 900 mm from the projected outline of the urinal on to the wall or floor.

(2)  Floor surfaces around a water closet shall be protected from deterioration by impervious and durable material for a distance not less than 900 mm from the projected outline of the water closet on to the floor.

3.7.4.13.  Floor Drains

(1)  A floor drain shall be installed in a washroom containing urinals equipped with automatic flushing devices.

3.7.4.14.  Grab Bar Installation

(1)  Grab bars that are installed shall resist a minimum load of 1.3 kN applied vertically or horizontally.

3.7.4.15.  Privacy

(1)  If a room contains not more than 1 water closet, the doorway to the room shall be provided with a full height door that is capable of being locked from the inside.

(2)  If a room contains no fewer than 2 water closets or at least 1 water closet and 1 urinal, the room shall be designed so that water closets, urinals and lavatories are not visible from the entrance to the room.

3.7.4.16.  Water Temperature Control

(1)  A water distribution system supplying hot water to plumbing fixtures shall conform to the requirements in Subsection 7.6.5.

3.7.4.17.  Drinking Water

(1)  On every floor where work will be performed and within 100 m of any area where work will be performed, potable water shall be provided from,

(a)	a fountain with an upward jet,

(b)	a tap from a piped water supply, or

(c)	a tap from a covered vessel.

3.7.4.18.  Pharmacies

(1)  Every pharmacy shall be provided with a sink with hot and cold potable water for washing utensils used in the preparation, service or storage of drugs.

3.7.5.  Health Care Facility Systems

3.7.5.1.  Electrical Systems

(1)  In anaesthetizing locations, electrical systems shall be designed, constructed, installed and tested in conformance with CSA Z32, “Essential Electrical Systems in Health Care Facilities”.

3.7.5.2.  Medical Gas Piping

(1)  All medical gas piping systems shall be designed, constructed, installed and tested in conformance with CAN/CSA-Z305.1, “Nonflammable Medical Gas Piping Systems”.

3.7.5.3.  Shielding of X-Ray Equipment

(1)  Every installation of an x-ray machine or of x-ray equipment in a building shall be shielded to protect any person who could be exposed to radiation inside and outside the building.

3.7.6.  Food Premises

3.7.6.1.  Application

(1)  The requirements of this Subsection apply to all food premises.

3.7.6.2.  Room Finishes

(1)  Except as provided in Sentence (2), floors and floor coverings shall be tight, smooth and non-absorbent in rooms where,

(a)	food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed, prepared, stored, displayed, handled, served, distributed, sold or offered for sale,

(b)	utensils are washed, or

(c)	washing fixtures or toilet fixtures are located.

(2)  Carpeting may be used in areas where food is served.

(3)  Wall and ceiling finishes of rooms and passageways shall be easy to clean.

3.7.6.3.  Location of Plumbing Fixtures

(1)  A room containing a water closet shall be located where,

(a)	it does not open directly into any room or area where food or drink for human consumption, or an ingredient of food or drink for human consumption, is intended to be stored, prepared, processed, distributed, served, sold or offered for sale, and

(b)	it is not necessary for the public to go through the food preparation areas to gain access to the plumbing fixtures.

(2)  Except as permitted in Sentence (3), a room containing plumbing fixtures for the public and employees in a restaurant shall be located in the restaurant.

(3)  A room containing plumbing fixtures for the public in Sentence (2) need not be located in the restaurant if,

(a)	the room is located in the building containing the restaurant, and

(b)	the distance of travel between the restaurant and the room is not more than 45 m.

3.7.6.4.  Lavatories, Appliances and Sinks

(1)  A separate lavatory for the handwashing of employees shall be constructed in a location convenient for employees in each manufacturing, processing and preparation area.

(2)  If equipment and facilities for the cleaning and sanitizing of utensils are provided, they shall consist of,

(a)	mechanical equipment, or

(b)	drainage racks of corrosion-resistant materials and,

(i)	a three-compartment sink or three sinks, or

(ii)	a two-compartment sink or two sinks, where the first compartment or sink can be used effectively for washing and rinsing and the second compartment or sink can be used effectively for sanitizing.

(3)  A retail food premises is exempt from compliance with this Article if its eating and drinking area does not exceed 56 m2 and any one or more of the following applies:

(a)	it is designed to sell only cold drinks in or from the original container,

(b)	it is designed to sell only frozen confections in the original package or wrapper,

(c)	it is designed to prepare and sell only hot beverages,

(d)	it is designed to prepare and sell only popped corn, roasted nuts or french-fried potatoes,

(e)	it is designed to sell only food or drink for human consumption that,

(i)	is pre-packaged at a premises other than the food premises at which it is being offered for sale, and

(ii)	is not capable of supporting the growth of pathogenic organisms or the production of the toxins of such organisms.

3.7.6.5.  Hot and Cold Water Supply

(1)  A hot and cold water supply shall be provided to,

(a)	every plumbing appliance and fixture required by Article 3.7.6.4.,

(b)	every area where food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed or prepared, and

(c)	every area where utensils are washed.

(2)  This Article does not apply to a retail food premises described in Sentence 3.7.6.4.(3).

3.7.6.6.  Employee Facilities

(1)  In a food premises, where dressing rooms are provided for employees, there shall be separate dressing rooms for males and females that,

(a)	are large enough for the employees to change and store their clothing, and

(b)	are equipped with lockers or other facilities suitable for storing the clothing of the employees.

(2)  Every room containing sanitary units for employees shall have a floor area not less than 2.3 m2.

3.7.6.7.  Sleeping Quarters

(1)  A room or space intended to be used as sleeping quarters shall not open directly into any room where food or drink for human consumption, or an ingredient of food or drink for human consumption, is manufactured, processed, prepared, stored, displayed, handled, served, distributed, sold or offered for sale.

Section 3.8.  Barrier-Free Design

3.8.1.  General

3.8.1.1.  Application

(1)  The requirements of this Section apply to all buildings except,

(a)	houses, including semi-detached houses, duplexes, triplexes, town houses, row houses and boarding or rooming houses with fewer than 8 boarders or roomers,

(b)	buildings of Group F, Division 1 major occupancy, and

(c)	buildings that are not intended to be occupied on a daily or full time basis, including automatic telephone exchanges, pumphouses and substations.

3.8.1.2.  Entrances

(1)  In addition to the barrier-free entrances required by Sentence (2), the number of barrier-free entrances in a building referred to in Sentence 3.8.1.1.(1) shall be no fewer than those as specified in Table 3.8.1.2. and shall lead from,

(a)	the outdoors at sidewalk level, or

(b)	a ramp that conforms to Article 3.8.3.4. and leads from a sidewalk.

(2)  A suite of assembly occupancy, business and personal services occupancy or mercantile occupancy that is located in the first storey of a building or in a storey to which a barrier-free path of travel is provided, and that is separated from the remainder of the building, so that there is no access to the remainder of the building, shall have at least one barrier-free entrance.

Table 3.8.1.2.
Minimum Number of Pedestrian Entrances Required to be Barrier-Free

Forming Part of Sentence 3.8.1.2.(1)

| Column 1 | Column 2 |
| --- | --- |
| Number of pedestrian entrances into building | Minimum number of pedestrian entrances required to be barrier-free |
| 1 to 3 | 1 |
| more than 3 to 5 | 2 |
| more than 5 | not less than 50 per cent |

(3)  A barrier-free entrance required by Sentences (1) or (2) shall be designed in accordance with Article 3.8.3.3.

(4)  At a barrier-free entrance that includes more than one doorway, only one of the doorways is required to be designed in accordance with the requirements of Article 3.8.3.3.

(5)  If a walkway or pedestrian bridge connects two barrier-free storeys in different buildings, the path of travel from one storey to the other storey by means of the walkway or bridge shall be barrier-free.

3.8.1.3.  Barrier-Free Path of Travel

(1)  Except as required in Sentence (4) and except as permitted in Subsection 3.8.3., every barrier-free path of travel shall provide an unobstructed width of at least 1 100 mm for the passage of wheelchairs.

(2)  Interior and exterior walking surfaces that are within a barrier-free path of travel shall,

(a)	have no opening that will permit the passage of a sphere more than 13 mm in diam,

(b)	have any elongated openings oriented approximately perpendicular to the direction of travel,

(c)	be stable, firm and slip-resistant,

(d)	be bevelled at a maximum slope of 1 in 2 at changes in level not more than 13 mm, and

(e)	be provided with sloped floors or ramps at changes in level more than 13 mm.

(3)  A barrier-free path of travel is permitted to include ramps, passenger elevators or other platform equipped passenger elevating devices to overcome a difference in level.

(4)  Every barrier-free path of travel less than 1 600 mm in width shall be provided with an unobstructed space not less than 1 600 mm in width and 1 600 mm in length located not more than 30 m apart.

(5)  Where the headroom of an area in a barrier-free path of travel is reduced to less than 1 980 mm, a guardrail or other barrier with its leading edge at or below 680 mm from the floor shall be provided.

3.8.1.4.  Access to Storeys Served by Escalators and Moving Walks

(1)  In a building in which an escalator or inclined moving walk provides access to any floor level above or below the entrance floor level, an interior barrier-free path of travel shall be provided to that floor level.

(2)  The route from the escalator or inclined moving walk to the barrier-free path of travel that leads from floor to floor required by Sentence (1) shall be clearly indicated by appropriate signs.

3.8.1.5.  Controls

(1)  Except as required by Sentences 3.5.2.2.(1) and 3.8.3.5.(1) for elevators and Sentence 3.8.3.3.(17) for power door operator controls, controls for the operation of building services or safety devices, including electrical switches, thermostats and intercom switches, intended to be operated by the occupant and located in a barrier-free path of travel shall be accessible to a person in a wheelchair, operable with one hand and mounted at not less than 900 mm and not more than 1 200 mm above the floor.

(2)  A signal intended for the public to indicate the operation of a building security system that controls access to a building shall consist of an audible and visual signal.

3.8.1.6.  Illumination

(1)  All portions of a barrier-free path of travel shall be equipped to provide a level of illumination in accordance with Sentence 3.2.7.1.(1).

3.8.2.  Occupancy Requirements

3.8.2.1.  Areas Requiring Barrier-Free Path of Travel

(1)  Except as permitted by Sentence (2), a barrier-free path of travel from the entrances required by Sentences 3.8.1.2.(1) and (2) to be barrier-free shall be provided throughout the entrance storey and within all other normally occupied floor areas served by a passenger elevator, escalator, inclined moving walk, or other platform equipped passenger elevating device.

(2)  The provision of a barrier-free path of travel in Sentence (1) does not apply,

(a)	to service rooms,

(b)	to elevator machine rooms,

(c)	to janitors rooms,

(d)	to service spaces,

(e)	to crawl spaces,

(f)	to attic or roof spaces,

(g)	to floor levels not served by a passenger elevator, a platform-equipped passenger-elevating device, an escalator, or an inclined moving walk,

(h)	to high hazard industrial occupancies,

(i)	within portions of a floor area with fixed seats in an assembly occupancy where these portions are not part of the barrier-free path of travel to spaces designated for wheelchair use,

(j)	into suites of residential occupancy that are in storeys other than the entrance storey and that have all entrance doors at floor levels that do not correspond to elevator stop levels,

(k)	except as required by Sentence (4) within a suite of residential occupancy, or

(l)	within those parts of a floor area that are not at the same level as the entry level, provided amenities and uses provided on any raised or sunken level are accessible on the entry level by means of a barrier-free path of travel.

(3)  The minimum number of spaces designated for wheelchair use in an assembly occupancy with fixed seats shall conform to Table 3.8.2.1.

(4)  In a Group C major occupancy apartment building, not less than 10% of all residential suites shall be provided with a barrier-free path of travel from the suite entrance door to,

(a)	the doorway to at least one bedroom at the same level, and

(b)	the doorway to at least one bathroom,

(i)	having an area not less than 4.5 m2 at the same level, and

(ii)	conforming to Sentence 9.6.3.3.(1).

Table 3.8.2.1.
Designated Wheelchair Spaces

Forming Part of Sentence 3.8.2.1.(4)

| Column 1 | Column 2 |
| --- | --- |
| Number of Fixed Seats in Seating Area | Minimum Number of Spaces Required for Wheelchairs |
| up to 100 | 2 |
| 101 to 200 | 3 |
| 201 to 300 | 4 |
| 301 to 400 | 5 |
| 401 to 600 | 6 |
| Over 600 | Not less than 1 per cent of the seating capacity |

3.8.2.2.  Access to Parking Areas

(1)  A barrier-free path of travel shall be provided from the entrance described in Article 3.8.1.2. to,

(a)	an exterior parking area, where exterior parking is provided, and

(b)	at least one parking level, where a passenger elevator serves an indoor parking level.

(2)  The vehicular entrance to and egress from at least one parking level described in Sentence (1) and all areas intended to be used by wheelchair accessible vehicles to gain access to a parking space on that level shall have a vertical clearance of not less than 2 100 mm.

(3)  If an exterior passenger loading zone is provided, it shall have,

(a)	an access aisle not less than 1 500 mm wide and 6 m long adjacent and parallel to the vehicle pull-up space,

(b)	a curb ramp, where there are curbs between the access aisle and the vehicle pull-up space, and

(c)	a clearance height of not less than 2 750 mm at the vehicle pull-up space and along the vehicle access and egress routes.

3.8.2.3.  Washrooms Required to be Barrier-Free

(1)  Except where other barrier-free washrooms are provided on the same floor level within 45 m and except within suites of residential occupancy, and buildings exempted in Clauses 3.8.1.1.(1)(a), (b) and (c), in buildings where a washroom is required in accordance with Subsection 3.7.4., a barrier-free path of travel shall be provided to a barrier-free washroom designed to accommodate disabled persons in conformance with the appropriate requirements in Articles 3.8.3.8. to 3.8.3.12.

(2)  Except as permitted in Sentence (3), where washrooms in excess of those required by Subsection 3.7.4. are provided in a storey to which a barrier-free path of travel is required in conformance with Article 3.8.2.1., these washrooms shall be designed to accommodate disabled persons in conformance with the appropriate requirements in Articles 3.8.3.8. to 3.8.3.12.

(3)  Washrooms need not conform to the requirements in Sentence (2) provided,

(a)	they are located within suites of residential occupancy,

(b)	other barrier-free washrooms are provided on the same floor level within 45 m, or

(c)	they are located in an individual suite that is,

(i)	used for a business and personal services occupancy, a mercantile occupancy or an industrial occupancy,

(ii)	less than 300 m2 in area, and

(iii)	completely separated from, and without access to, the remainder of the building.

3.8.2.4. Hotels

(1)  Except as permitted in Sentence (2), at least 10% of the suites of a hotel shall,

(a)	have a barrier-free path of travel extending to the inside of each room, and to a balcony where required by Sentence 3.3.1.7.(2), and

(b)	be distributed among storeys having a barrier-free path of travel.

(2)  Not more than 20 suites need comply with Sentence (1).

(3)  A suite having a barrier-free path of travel required by Sentence (1) shall have a bathroom that,

(a)	conforms to the requirements of Clauses 3.8.3.12.(1)(a) to (i),

(b)	has an unobstructed area at least 1 200 mm in diameter extending the full height of the room; however, a door is permitted to open on the inside if it does not reduce the unobstructed area, and

(c)	has a bath or shower that conforms to the requirements of Article 3.8.3.13.

3.8.3.  Design Standards

3.8.3.1.  Accessibility Signs

(1)  Where a building is required to have a barrier-free entrance to accommodate disabled persons, signs incorporating the International Symbol of Accessibility shall be installed where necessary to indicate,

(a)	the location of that entrance, and

(b)	the location of ramps located in a required barrier-free path of travel serving that entrance.

(2)  Where a washroom, elevator, telephone or parking area is required to accommodate disabled persons, it shall be identified by a sign consisting of the international symbol of accessibility for disabled persons and such other graphic, tactile or written directions as are needed to indicate clearly the type of facility available.

(3)  Where a washroom is not designed to accommodate disabled persons in a storey to which a barrier-free path of travel is required, signs shall be provided to indicate the location of the barrier-free facilities.

(4)  Signs incorporating the international symbol of accessibility for disabled persons shall be installed where necessary to indicate the location of the accessible means of egress.

(5)  Characters, symbols or pictographs on tactile signs shall, if wall mounted, be located not less than 1 200 mm and not more than 1 500 mm above the floor.

3.8.3.2.  Exterior Walks

(1)  Except as provided in Sentence (2), exterior walks that form part of a barrier-free path of travel shall,

(a)	be provided by means of a continuous plane not interrupted by steps or abrupt changes in level,

(b)	have a permanent, firm and slip-resistant surface,

(c)	except as required in Sentence 3.8.1.3.(4), have an uninterrupted width of not less than 1 100 mm and a gradient not exceeding 1 in 20,

(d)	be designed as a ramp where the gradient is greater than 1 in 20,

(e)	have not less than 1 100 mm wide surface of a different texture to that surrounding it, where the line of travel is level and even with adjacent walking surfaces,

(f)	be free from obstructions for the full width of the walk to a minimum height of 1 980 mm, except that handrails are permitted to project not more than 100 mm from either side into the clear area, and

(g)	have a level area adjacent to the entrance doorway conforming to Clause 3.8.3.4.(1)(c).

(2)  Where a difference in elevation between levels in a walkway is not more than 200 mm, a curb ramp conforming to Sentences (3) and (4) may be provided.

(3)  The curb ramp permitted by Sentence (2) shall,

(a)	have a running slope conforming to Table 3.8.3.2.,

(b)	have a width of not less than 1 200 mm exclusive of flared sides,

(c)	have a surface including flared sides that shall,

(i)	be slip-resistant,

(ii)	have a detectable warning surface that is colour- and texture-contrasted with the adjacent surfaces, and

(iii)	have a smooth transition from the ramp and adjacent surfaces, and

(d)	have flared sides with a slope of not more than 1:10 where pedestrians are likely to walk across them.

Table 3.8.3.2.
Ramp Rise and Slope

Forming Part of Sentence 3.8.3.2.(3)

| Column 1 | Column 2 |
| --- | --- |
| Vertical Rise Between Surfaces, mm | Slope |
| 75 to 200 | 1:10 to 1:12 |
| less than 75 | 1:8 to 1:10 |

(4)  Curb ramps described in Sentence (3) do not require handrails or guards.

3.8.3.3.  Doorways and Doors

(1)  Every doorway that is located in a barrier-free path of travel shall have a clear width of not less than 850 mm when the door is in the open position.

(2)  Except where no bathroom within the suite is at the level of the suite entrance door to which a barrier-free path of travel is provided in accordance with Sentence 3.8.2.1.(1), the doorway to at least 1 bathroom and to each bedroom at the same level as such bathroom within a suite of residential occupancy shall have, when the door is in the open position, a clear width of not less than,

(a)	760 mm where the door is served by a corridor or space not less than 1 060 mm wide, and

(b)	810 mm where the door is served by a corridor or space less than 1 060 mm wide

(3)  Door opening devices that are the only means of operation shall be of a design that does not require tight grasping and twisting of the wrist.

(4)  Except as permitted by Sentences (6) and (12), every door that provides a barrier-free path of travel through an entrance referred to in Article 3.8.1.2. shall be equipped with a power door operator if the entrance serves,

(a)	a hotel,

(b)	a building containing a Group B, Division 2 or 3 occupancy, or

(c)	a building more than 300 m2 in building area containing a Group A, D or E occupancy.

(5)  Except as permitted by Sentences (6) and (12), where the entrance described in Article 3.8.1.2. incorporates a vestibule, a door leading from the vestibule into the floor area shall be equipped with a power door operator in,

(a)	a hotel,

(b)	a building of Group B, Division 2 or 3, occupancy, and

(c)	a building more than 300 m2 in building area containing a Group A, D or E occupancy.

(6)  The requirements in Sentence (4) and (5) do not apply to an individual suite having an area of less than 300 m2 in buildings having only suites of Group A, D or E occupancy where such suite is completely cut off from the remainder of the building.

(7)  Except as permitted in Sentence (8), and except for doors with power operators, closers for doors in a barrier-free path of travel shall be designed to permit doors to open when a force of not more than 38 N is applied to the handles, push plates or latch-releasing devices in the case of exterior doors and 22 N in the case of interior doors

(8)  Sentence (7) does not apply to doors at the entrances to dwelling units, or where greater forces are required in order to close and latch the doors against prevailing differences in air pressures on opposite sides of the doors.

(9)  Except for doors at the entrances to dwelling units, closers for interior doors in a barrier-free path of travel shall have a closing period of not less than 3 seconds measured from when the door is in an open position of 70° to the doorway, to when the door reaches a point 75 mm from the closed position, measured from the leading edge of the latch side of the door.

(10)  Unless equipped with a power door operator, a door in a barrier-free path of travel shall have a clear space on the latch side extending the height of the doorway and not less than,

(a)	600 mm beyond the edge of the door opening if the door swings toward the approach side, and

(b)	300 mm beyond the edge of the door opening if the door swings away from the approach side.

(11)  Vestibules located in a barrier-free path of travel shall be arranged to allow the movement of wheelchairs between doors and shall provide a distance between 2 doors in series of at least 1 200 mm plus the width of any door that swings into the space in the path of travel from one door to another.

(12)  Only the active leaf in a multiple leaf door in a barrier-free path of travel need conform to the requirements of this Article.

(13)  Except as provided in Clause 3.8.3.4.(1)(c), the floor surface on each side of a door in a barrier-free path of travel shall be level within a rectangular area ,

(a)	as wide as the door plus the clearance required on the latch side by Sentence (10), and

(b)	whose dimension perpendicular to the closed door is not less than the width of the barrier-free path of travel but need not exceed 1 500 mm.

(14)  Where a vision panel is provided in a door in a barrier-free path of travel, such panel shall be at least 75 mm in width and be located so that,

(a)	the bottom of the panel is not more than 900 mm above the finished floor, and

(b)	the edge of the panel closest to the latch is not more than 250 mm from the latch side of the door.

(15)  A door in a barrier-free path of travel consisting of a sheet of glass shall be marked with a continuous opaque strip that,

(a)	shall be colour and brightness contrasted to the background of the door,

(b)	shall be at least 50 mm wide,

(c)	shall be located across the width of the door at a height of 1 350 mm to 1 500 mm above the finished floor, and

(d)	may incorporate a logo or symbol provided such logo or symbol does not diminish,

(i)	the opacity of the strip,

(ii)	the width of the strip,

(iii)	the colour and brightness contrast of the strip to the background of the door, and

(iv)	the continuity of the strip across the width of the door.

(16)  The power door operator required by Sentences (4) and (5) shall allow persons to activate the opening of the door from either side.

(17)  The control for a power door operator required by Sentences (4) and (5) shall,

(a)	have no face dimension less than 100 mm,

(b)	have its centre located not less than 1000 mm and not more than 1100 mm from the floor level or ground,

(c)	be located not less than 600 mm beyond the door swing where the door opens towards the control, and

(d)	contain the sign incorporating the International Symbol of Accessibility.

3.8.3.4.  Ramps

(1)  Ramps located in a barrier-free path of travel shall,

(a)	have a minimum width of 900 mm between handrails,

(b)	have a maximum gradient of 1 in 12,

(c)	have a level area of at least 1 670 mm by 1 670 mm at the top and bottom of a ramp and where a door is located in a ramp, so that the level area extends at least 600 mm beyond the latch side of the door opening, except that where the door opens away from the ramp, the area extending beyond the latch side of the door opening may be reduced to 300 mm,

(d)	have a level area at least 1 670 mm long and at least the same width as the ramp,

(i)	at intervals of not more than 9 m along its length, and

(ii)	where there is an abrupt change in the direction of the ramp,

(e)	except as provided in Sentence (2), be equipped with handrails on both sides that shall,

(i)	be continuously graspable along their entire length and have circular cross-section with an outside diameter not less than 30 mm and not more than 40 mm, or any non-circular shape with a graspable portion that has a perimeter not less than 100 mm and not more than 155 mm and whose largest cross-sectional dimension is not more than 57 mm,

(ii)	be not less than 865 mm and not more than 965 mm high, measured vertically from the surface of the ramp, except that handrails not meeting these requirements are permitted provided they are installed in addition to the required handrail,

(iii)	be terminated in a manner that will not obstruct pedestrian travel or create a hazard,

(iv)	extend horizontally not less than 300 mm beyond the top and bottom of the ramp,

(v)	be provided with a clearance of not less than 40 mm between the handrail and any wall to which it is attached, and

(vi)	be designed and constructed such that handrails and their supports will withstand the loading values obtained from the nonconcurrent application of a concentrated load not less than 0.9 kN applied at any point and in any direction for all handrails and a uniform load not less than 0.7 kN/m applied in any direction to the handrail,

(f)	except as provided in Sentence (2), have a wall or a guard on both sides and where a guard is provided the guard shall,

(i)	be not less than 1 070 mm measured vertically to the top of the guard from the ramp surface, and

(ii)	be designed so that no member, attachment or opening located between 140 mm and 900 mm above the ramp surface being protected by the guard will facilitate climbing, and

(g)	be provided,

(i)	with a curb at least 50 mm high on any side of the ramp where no solid enclosure or solid guard is provided, and

(ii)	with railings or other barriers that extend to within 50 mm of the finished ramp surface or have a curb not less than 50 mm high.

(2)  Where a ramp serves as an aisleway for fixed seating, the requirements for handrails in Clause (1)(e) need not apply.

(3)  Floors or walks in a barrier-free path of travel having a slope steeper than 1 in 20 shall be designed as ramps.

3.8.3.5.  Passenger Elevating Devices

(1)  A passenger elevating device referred to in Article 3.8.2.1. shall conform to CAN/CSA-B355, “Lifts for Persons with Physical Disabilities”.

3.8.3.6.  Spaces in Seating Area

(1)  Spaces designated for wheelchair use in Sentence 3.8.2.1.(3) shall be,

(a)	clear and level or level with removable seats,

(b)	not less than 900 mm wide and 1 525 mm long to permit a wheelchair to enter from a side approach, and 1 220 mm long where the wheelchair enters from the front or rear of the space,

(c)	arranged so that at least two designated spaces are side by side,

(d)	located adjoining a barrier-free path of travel without infringing on egress from any row of seating or any aisle requirements, and

(e)	situated, as part of the designated seating plan, to provide a choice of viewing location and a clear view of the event taking place.

3.8.3.7.  Assistive Listening Devices

(1)  In buildings of assembly occupancy, all classrooms, auditoria, meeting rooms and theatres with an area of more than 100 m2 and an occupant load of more than 75 shall be equipped with assistive listening systems encompassing the entire seating area.

3.8.3.8.  Water Closet Stalls

(1)  Where a washroom is required by Article 3.8.2.3. to be barrier-free, at least 1 water closet stall or enclosure shall,

(a)	be at least 1 500 mm in width by 1 500 mm in depth,

(b)	be equipped with a door that shall,

(i)	be capable of being latched from the inside with a mechanism that is operable by one hand,

(ii)	provide, when the door is in an open position, a clear opening of at least 810 mm,

(iii)	swing outward, unless 760 mm by 1 220 mm clear floor area is provided within the stall or enclosure to permit the door to be closed without interfering with the wheelchair,

(iv)	be provided with spring-type or gravity hinges so that the door closes automatically,

(v)	be provided with a door pull on the outside, near the latch side of the door, and

(vi)	be aligned with the clear manoeuvring space adjacent to the water closet,

(c)	have a water closet located so that its centreline is not less than 460 mm and not more than 480 mm from an adjacent side wall on one side,

(d)	be equipped with grab bars that shall,

(i)	be at least 760 mm in length and mounted at a 30° to 50° angle sloping upwards, away from the water closet with the lower end of the bar mounted 750 mm to 900 mm above the floor and 50 mm in front of the toilet bowl, or alternatively, be L-shaped with 760 mm long horizontal and vertical components mounted with the horizontal component 750 mm to 900 mm above the floor and the vertical component 150 mm in front of the toilet bowl,

(ii)	be at least 600 mm in length mounted horizontally on the wall behind the water closet from 840 mm to 920 mm above the floor and, where the water closet has a water tank, be mounted 150 mm above the tank,

(iii)	Reserved

(iv)	be installed to resist a load of at least 1.3 kN applied vertically or horizontally,

(v)	be not less than 30 mm and not more than 40 mm in diameter,

(vi)	have a clearance of 30 mm to 40 mm from the wall, and

(vii)	have a slip resistant surface,

(e)	be equipped with a coat hook mounted not more than 1 200 mm above the floor on a side wall and projecting not more than 50 mm from the wall,

(f)	have a clearance of at least 1 700 mm between the outside of the stall face and the face of an in-swinging washroom door and 1 400 mm between the outside of the stall face and any wall-mounted fixture or other obstruction, and

(g)	when a toilet paper dispenser is provided, provide a dispenser that is,

(i)	wall mounted,

(ii)	located below the grab bar,

(iii)	in line with or not more than 300 mm in front of the toilet seat, and

(iv)	not less than 600 mm above the floor.

3.8.3.9.  Water Closets

(1)  Water closets for a person with physical disabilities shall,

(a)	be equipped with a seat located at not less than 400 mm and not more than 460 mm above the floor,

(b)	be equipped with hand-operated flushing controls that are easily accessible to a wheelchair user or be automatically operable,

(c)	be equipped with a back support where there is no seat lid or tank, and

(d)	not have a spring-activated seat.

3.8.3.10.  Reserved

3.8.3.11.  Lavatories

(1)  A barrier-free washroom shall be provided with a lavatory that shall,

(a)	be located so that the distance between the centreline of the lavatory and the side wall is not less than 460 mm,

(b)	be mounted so that the top of the lavatory or, where the lavatory is in a vanity, the top of the vanity is not more than 840 mm above the finished floor,

(c)	have a clearance beneath the lavatory not less than,

(i)	760 mm wide,

(ii)	735 mm high at the front edge,

(iii)	685 mm high at a point 205 mm back from the front edge, and

(iv)	230 mm high over the distance from a point 280 mm to a point 430 mm back from the front edge,

(d)	have insulated pipes where they would otherwise present a burn hazard or have water supply temperature limited to a maximum of 43°C,

(e)	be equipped with faucet handles of the lever type without spring loading or be automatically operable and are located so that the distance from the centreline of the faucet to the edge of the basin or, where the basin is mounted in a vanity, to the front edge of the vanity, is not more than 485 mm, and

(f)	have soap dispensers that are,

(i)	located to be accessible to persons in wheelchairs,

(ii)	located so that the dispensing height is not more than 1 200 mm above the floor, and

(iii)	operable with one hand.

(g)	have towel dispensers or other hand drying equipment that are,

(i)	located to be accessible to persons in wheelchairs,

(ii)	located so that the dispensing height is not more than 1 200 mm above the floor, and

(iii)	operable with one hand.

(2)  If mirrors are provided in a barrier-free washroom, at least one mirror shall be,

(a)	mounted with its bottom edge not more than 1 000 mm above the floor, or

(b)	inclined to the vertical to be usable by a person in a wheelchair.

(3)  If dispensing or hand-operated washroom accessories, except those located in toilet stalls or described in Clause (1)(f), are provided, they shall be mounted so that the dispensing height is between 900 mm and 1 200 mm above the floor.

3.8.3.12.  Universal Toilet Rooms

(1)  A universal toilet room shall,

(a)	be served by a barrier-free path of travel,

(b)	have a door capable of being locked from the inside and released from the outside in case of emergency and that has,

(i)	a graspable latch-operating mechanism located not less than 900 mm and not more than 1 000 mm above the floor,

(ii)	if it is an outward swinging door, a door pull not less than 140 mm long located on the inside so that its midpoint is not less than 200 mm and not more than 300 mm from the hinged side of the door and not less than 900 mm and not more than 1 000 mm above the floor, and

(iii)	if it is an outward swinging door, a door closer, spring hinges or gravity hinges, so that the door closes automatically,

(c)	have one lavatory conforming to Article 3.8.3.11.,

(d)	have one water closet conforming to the requirements of Article 3.8.3.9. and located,

(i)	so that its centreline is not less than 460 mm and not more than 480 mm from an adjacent side wall on one side, and

(ii)	not less than 1 020 mm to the wall on the other side,

(e)	have grab bars conforming to Clause 3.8.3.8.(1)(d),

(f)	have no internal dimension between walls that is less than 1 700 mm,

(g)	have a coat hook conforming to Clause 3.8.3.8.(1)(e) and a shelf located not more than 1 200 mm above the floor,

(h)	be designed to permit a wheelchair to back in alongside the water closet in the space referred to in Subclause (d)(ii),

(i)	be designed to permit a wheelchair to turn in an open space not less than 1 500 mm in diameter, and

(j)	be provided with a door equipped with a power door operator if the door is equipped with a self-closing device.

(2)  Reserved.

3.8.3.13.  Showers and Bathtubs

(1)  Except within a suite of residential occupancy, if showers are provided in a building, at least one shower stall in each group of showers shall be barrier-free and shall,

(a)	be not less than 1 500 mm wide and 900 mm deep,

(b)	have a clear floor space at the entrance to the shower not less than 900 mm deep and the same width as the shower, except that fixtures are permitted to project into that space provided they do not restrict access to the shower,

(c)	have a slip-resistant floor surface,

(d)	have a bevelled threshold not more than 13 mm higher than the finished floor,

(e)	have a hinged seat that is not spring-loaded or a fixed seat that shall be,

(i)	not less than 450 mm wide and 400 mm deep,

(ii)	mounted approximately 450 mm above the floor, and

(iii)	designed to carry a minimum load of 1.3 kN,

(f)	have a horizontal grab bar conforming to Subclauses 3.8.3.8.(1)(d)(iv) to (vi) that is,

(i)	not less than 900 mm long,

(ii)	mounted approximately 850 mm above the floor, and

(iii)	located on the wall opposite the entrance to the shower so that not less than 300 mm of its length is at one side of the seat,

(g)	have a pressure-equalizing or thermostatic mixing valve controlled by a lever or other device operable with a closed fist from the seated position,

(h)	have a hand-held shower head with not less than 1 500 mm of flexible hose located so that it can be reached from the seated position and equipped with a support so that it can operate as a fixed shower head, and

(i)	have fully recessed soap holders that can be reached from the seated position.

(2)  Individual shower stalls that are provided for use by patients or residents in buildings of Group B, Division 2 or 3 occupancy shall conform to the requirements of Sentence (1).

(3)  Individual bathtubs that are provided for the use of patients or residents in buildings of Group B, Division 2 or 3 occupancy shall have,

(a)	faucet handles of the lever type that are not spring-loaded or be automatically operable,

(b)	faucet handles that are located so as to be usable by a person seated in the bathtub, and

(c)	unless the bathtub is free-standing, an “L”-shaped grab bar conforming to Subclauses 3.8.3.8.(1)(d)(iv) to (vi) mounted on the wall,

(i)	with each leg of the “L” being at least 900 mm long,

(ii)	with the legs of the “L” being separated by 90°,

(iii)	with the horizontal leg of the “L” being located between 150 mm and 200 mm above and parallel to the rim of the bathtub, and

(iv)	with the vertical leg of the “L” being located between 300 mm and 450 mm from the control end of the bathtub.

3.8.3.14.  Reserved

3.8.3.15.  Shelves or Counters for Telephones

(1)  Where built-in shelves or counters are provided for public telephones, they shall be level and shall,

(a)	be not less than 350 mm deep, and

(b)	have, for each telephone provided, a clear space not less than 250 mm wide having no obstruction within 250 mm above the surface.

(2)  The top surface of a section of the shelf or counter described in Sentence (1) serving at least one telephone shall,

(a)	be not more than 865 mm from the floor, and

(b)	have a knee space not less than 685 mm high.

(3)  Where a wall-hung telephone is provided above the shelf or counter section described in Sentence (2), it shall be located so that the receiver and coin slot are not more than 1 200 mm from the floor.

3.8.3.16.  Drinking Fountains

(1)  Where drinking fountains are provided, at least one shall be barrier-free and shall,

(a)	have a spout located near the front of the unit not more than 915 mm above the floor, and

(b)	be equipped with controls that are easily operated from a wheelchair using one hand with a force of not more than 22 N or be automatically operable.

Section 3.9.  Portable Classrooms

3.9.1.  Scope

3.9.1.1.  Application

(1)  Except as provided in this Section, the requirements in this Division apply to portable classrooms.

3.9.1.2.  Heating Systems

(1)  Heating systems and equipment in a portable classroom shall be designed and installed in accordance with Section 6.2.

3.9.2.  Interior Finish

3.9.2.1.  Flame-Spread Rating

(1)  Interior finish material used on a wall or ceiling of a portable classroom shall have a flame-spread rating of 150 or less.

3.9.3.  Application

3.9.3.1.  Building Areas

(1)  A single portable classroom shall be not more than 100 m2 in building area, and not more than 1 storey in building height.

(2)  For the purposes of Subsection 3.2.2., where the horizontal distance between portable classrooms is less than 6 m, a group of portable classrooms may be considered as a single building with a building area equal to the aggregate area of the portable classrooms.

3.9.3.2.  Spatial Separations

(1)  The requirements in Subsection 3.2.3. need not be provided between individual portable classrooms where the distance between the classrooms is 6 m or more.

(2)  The requirements in Subsection 3.2.3. need not be provided between individual portable classrooms within a group where,

(a)	the portable classrooms are in groups where ,

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group is not more than 6, and

(iii)	the distance between groups of classrooms is 12 m or more, or

(b)	the portable classrooms are in groups where,

(i)	the means of egress for each classroom within a group is by a common corridor or passageway,

(ii)	the number of portable classrooms in a group is not more than 6, and

(iii)	the distance between groups of portable classrooms is 12 m or more.

3.9.3.3.  Fire Alarm Systems

(1)  Except as provided in Sentences (2) and (3), the fire alarm system in the main school building shall be extended to the portable classrooms with a separate zone indicator on the annunciator.

(2)  The requirements in Sentence (1) need not be provided where there are not more than 12 portables on a site and where,

(a)	Reserved

(b)	the distance between portable classrooms is less than 6 m and the requirements of Subsection 3.2.3. are applied between the classrooms, or

(c)	the portable classrooms are in groups where,

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group does not exceed 6,

(iii)	within a group of classrooms, the facing walls have a fire-resistance rating of 45 min, rated from inside the classroom, and

(iv)	the distance between groups of classrooms is 12 m or more.

(3)  The requirements in Sentence (1) need not be provided where the distance between portable classrooms is 6 m or more.

3.9.3.4.  Provisions for Fire Fighting

(1)  The requirements in Articles 3.2.2.10. and 3.2.5.1. to 3.2.5.7. need not be provided where there are not more than 12 portable classrooms on a site and where,

(a)	the distance between portable classrooms is 6 m or more,

(b)	the distance between portable classrooms is less than 6 m and the requirements of Subsection 3.2.3. are applied between the classrooms,

(c)	the portable classrooms are in groups where,

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group is not more than 6,

(iii)	within a group of classrooms, the facing walls have a fire-resistance rating of 45 min, rated from inside the classroom, and

(iv)	the distance between groups of classrooms is 12 m or more,

(d)	the portable classrooms are in groups where,

(i)	the distance between the classrooms is less than 6 m,

(ii)	the number of classrooms in a group is not more than 6, and

(iii)	the distance between groups of classrooms is 12 m or more, or

(e)	the portable classrooms are in groups where,

(i)	the means of egress for each classroom within a group is by a common corridor or passageway,

(ii)	the number of classrooms in a group is not more than 6, and

(iii)	the distance between groups of classrooms is 12 m or more.

3.9.3.5.  Portable Fire Extinguishers

(1)  A fire extinguisher, in accordance with Article 3.2.5.17., shall be installed in each portable classroom.

3.9.3.6.  Means of Egress

(1)  Except as required in Sentence 3.9.3.7.(1), a portable classroom shall be provided with means of egress conforming to Sections 3.3. and 3.4.

3.9.3.7.  Fuel-Fired Appliances

(1)  Where there is only one egress door from a portable classroom, a fuel-fired appliance shall be separated from the remainder of the classroom by a fire separation with a fire-resistance rating of not less than 45 min.

(2)  Except as provided in Sentences (3) and (4), if a portable classroom contains a fuel-fired appliance, the appliance shall be separated from the remainder of the classroom by a fire separation having a fire-resistance rating not less than,

(a)	1.5 h where the horizontal distance between portable classrooms is 1 500 mm or less, and

(b)	45 min where the horizontal distance between portable classrooms is more than 1 500 mm.

(3)  If the horizontal distance between portable classrooms is 6 m or more, a fuel-fired appliance need not be separated from the remainder of the classroom by a fire separation provided,

(a)	there is not more than 1 appliance per portable classroom, and

(b)	the appliance is located not less than 4.5 m from an egress doorway or an exit from the portable classroom.

(4)  Fuel-fired appliances with sealed combustion located in a portable classroom are not required to be separated from the remainder of the classroom,

(a)	if there are not more than four portable classrooms in a group, and

(b)	if the appliance is located not less than 4.5 m from an egress doorway or an exit from the portable classroom.

3.9.3.8.  Washroom Facilities

(1)  Washroom facilities need not be provided in a portable classroom where the facilities in the main school building comply with the requirements of Subsection 3.7.4. for the total occupant load of the main school building and the portable classrooms.

3.9.3.9.  Barrier-Free Access

(1)  The requirements of Section 3.8. for barrier-free access need not be provided for a portable classroom provided that the main school building complies with the requirements of Section 3.8.

Section 3.10.  Self-Service Storage Buildings

3.10.1.  Scope

3.10.1.1.  Application

(1)  Except as provided in this Section, the requirements in this Division apply to self-service storage buildings.

3.10.2.  Requirements for All Buildings

3.10.2.1.  Occupancy Classification

(1)  A self-service storage building,

(a)	shall comply with the requirements for a Group F, Division 2 major occupancy, and

(b)	shall not contain a Group F, Division 1 occupancy.

3.10.2.2.  Occupant Load

(1)  The requirements based on occupant load shall not apply.

3.10.2.3.  Structural Fire Protection

(1)  Except as provided in Sentence (2) and Sentence 3.10.4.2.(1), the requirements in Subsections 3.2.1. and 3.2.2. shall apply.

(2)  The first storey shall be subdivided into areas not more than 500 m2 by a masonry or reinforced concrete fire separation having a fire-resistance rating not less than 1 h, or it shall be sprinklered.

3.10.2.4.  Safety Requirements Within Floor Areas

(1)  Except as provided in Sentences (2) to (12), the requirements in Section 3.3. shall apply.

(2)  A corridor need not be constructed as a public corridor where the travel distance, measured from inside the rental space to the nearest exit, is not more than 15 m provided that the corridor walls,

(a)	are of noncombustible construction,

(b)	have no openings other than doors and the doors are of solid construction, and

(c)	are continuous from the floor to the underside of the floor above, the ceiling or the roof.

(3)  Where the building is sprinklered, doors in a public corridor do not require to be equipped with self-closing devices and latches provided that the travel distance is measured from inside the rental space to the nearest exit.

(4)  Egress doors from a rental space are not required to swing in the direction of exit travel or swing on a vertical axis provided,

(a)	the area of the rental space is not more than 50 m2, and

(b)	the distance of travel within the rental space is not more than 10 m.

(5)  Where egress doors from a rental space open onto a corridor and swing in the direction of exit travel, the corridor shall be not less than 1 500 mm wide, and the doors shall be not more than 914 mm wide.

(6)  Where egress doors from a rental space open onto a corridor and do not swing in the direction of exit travel, the corridor shall be not less than 1 100 mm in width.

(7)  Dead end corridors are not permitted.

(8)  Corridors shall be provided with,

(a)	natural lighting that shall be uniformly distributed and be at least 4% of the corridor area, or

(b)	emergency lighting, conforming to Sentences 3.2.7.4.(1) and (2), that shall provide average levels of illumination not less than 10 lx at floor level.

(9)  Not more than two dwelling units shall be contained within one of the buildings on the property.

(10)  Dwelling units shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h.

(11)  A fire separation is not required between a dwelling unit and an office where the office is not more than 50 m2 in area.

(12)  The fire separations required in Sentence 3.3.1.1.(1) need not be provided between individual rental spaces.

3.10.2.5.  Exit Requirements

(1)  Except as provided in Sentences (2) and (3), the requirements in Section 3.4. shall apply.

(2)  The clear width of an exit stair shall be not less than 1 100 mm.

(3)  Exit doors from rental spaces are not required to swing on a vertical axis provided,

(a)	the area of the rental space is not more than 50 m2, and

(b)	the travel distance within the rental space is not more than 10 m.

3.10.2.6.  Service Facilities

(1)  Except as provided in Sentence (2), the requirements in Section 3.6. shall apply.

(2)  Except where located in and serving only the dwelling units, a fuel-fired appliance shall be located in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

3.10.2.7.  Sanitary Facilities

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.7.4. shall apply.

(2)  Except as permitted in Sentences 3.7.4.1.(2) and (3), two washrooms, each containing a water closet and a lavatory, shall be provided within one of the buildings on the property.

3.10.3.  Additional Requirements for Buildings Containing more than 1 Storey

3.10.3.1.  Application

(1)  The requirements in this Subsection apply to all buildings except a 1 storey building that does not contain a basement or mezzanine.

3.10.3.2.  Spatial Separations

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.2.3. shall apply.

(2)  The distance between buildings shall be not less than 9 m.

3.10.3.3.  Fire Alarm Systems

(1)  Except as provided in Sentences (2) and (3), the requirements in Subsection 3.2.4. shall apply.

(2)  A fire alarm system shall be installed.

(3)  Within the first storey, manual pull stations are required only in corridors.

3.10.3.4.  Provisions for Fire Fighting

(1)  Except as provided in Sentences (2) to (4), the requirements in Subsection 3.2.5. shall apply.

(2)  Access routes for fire department vehicles shall be provided and shall be not less than 9 m wide.

(3)  Hydrants shall be located in the access routes required in Sentence (2) so that,

(a)	for a building provided with a fire department connection for a standpipe system or a sprinkler system,

(i)	a fire department pumper vehicle can be located adjacent to a hydrant, and

(ii)	the unobstructed path of travel for the fire fighter from the vehicle to the fire department connection is not more than 45 m, and

(b)	for a building that is not sprinklered, a fire department pumper vehicle can be located in the access route so that the unobstructed path of travel for the fire fighter is not more than,

(i)	45 m from the hydrant to the vehicle, and

(ii)	45 m from the vehicle to every opening in the building.

3.10.3.5.  Standpipe Systems

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.2.9. shall apply.

(2)  Hose stations are not required in the first storey.

3.10.4.  Additional Requirements for 1 Storey Buildings

3.10.4.1.  Application

(1)  The requirements in this Subsection apply to 1 storey buildings that do not contain a basement or mezzanine.

3.10.4.2.  Building Area

(1)  For the purposes of Subsection 3.2.2., building area means,

(a)	the building area of each building,

(b)	the total of the building areas of all buildings as a group, or

(c)	the total of the building areas of any number or group of buildings.

3.10.4.3.  Spatial Separations

(1)  Except as provided in Sentences (2) to (4), the requirements in Subsection 3.2.3. shall apply.

(2)  Where the building area conforms to Clause 3.10.4.2.(1)(b), the limiting distance requirements shall not apply between individual buildings.

(3)  Where the building area conforms to Clause 3.10.4.2.(1)(c),

(a)	the limiting distance requirements shall apply between each group of buildings, but not between individual buildings within a group, and

(b)	the distance between each group of buildings shall be not less than 9 m.

(4)  The distance between individual buildings within a group shall be not less than 6 m.

3.10.4.4.  Fire Alarm Systems

(1)  Except as provided in Sentence (2), the requirements in Subsection 3.2.4. shall not apply.

(2)  The requirements for smoke alarms in Article 3.2.4.21. shall apply to a dwelling unit.

3.10.4.5.  Provisions for Fire Fighting

(1)  Except as provided in Sentences (2) to (7), the requirements in Subsection 3.2.5. shall not apply.

(2)  Access routes for fire department vehicles shall be provided and shall be not less than 9 m wide.

(3)  Hydrants shall be located in the access routes required in Sentence (2) so that the locations conform to Sentence 3.10.3.4.(3).

(4)  The access routes required in Sentence (2) shall conform to the requirements in Sentence 3.2.5.6.(1).

(5)  An adequate water supply for fire fighting shall be provided for every building.

(6)  Where a sprinkler system is installed, the system shall conform to the requirements in Articles 3.2.5.13., 3.2.5.16. and 3.2.5.18.

(7)  Where combustible sprinkler piping is installed, it shall conform to the requirements in Article 3.2.5.14.

Section 3.11.  Public Pools

3.11.1.  General

3.11.1.1.  Application

(1)  This Section applies to every public pool.

(2)  This Section applies to the design and construction of site assembled and manufactured pools that are intended for use as public pools.

(3)  Where material alterations to a public pool or the equipment installed in a public pool affect the bottom slope, the water volume or the capacity of the recirculation system, the adversely affected portions shall comply with the requirements of this Division.

(4)  Where material alterations or repairs concern any pool fitting passing water and/or air in or out of the pool tank, the affected fitting shall comply with Sentences 3.11.8.1.(14) to (20).

3.11.2.  Designations of Public Pools

3.11.2.1.  Pool Designations

(1)  Every public pool shall be designated as being either a Class A pool or a Class B pool in accordance with Sentence (2) or (3).

(2)  A Class A pool is a public pool to which the general public is admitted or that is,

(a)	operated in conjunction with or as a part of a program of an educational, instructional, physical fitness or athletic institution or association, supported in whole or in part by public funds or public subscription, or

(b)	operated on the premises of a recreational camp, for use by campers and their visitors and camp personnel.

(3)  A Class B pool is a public pool that is,

(a)	operated in conjunction with six or more dwelling units, suites, single family residences, or any combination of them for the use of occupants or residents and their visitors,

(b)	operated in conjunction with a mobile home park for the use of residents or occupants and their visitors,

(c)	operated on the premises of a hotel for the use of its guests and their visitors,

(d)	operated on the premises of a campground for the use of its tenants and their visitors,

(e)	operated in conjunction with a club for the use of its members and their visitors, or

(f)	operated in conjunction with an establishment or institution classified in Table 3.1.2.1. as,

(i)	Group B, Division 1, major occupancy, or

(ii)	Group B, Division 2 or 3, major occupancy, for the use of residents or occupants and their visitors.

3.11.3.  Pool and Pool Deck Design and Construction Requirements for all Class A and Class B Pools

3.11.3.1.  Construction Requirements

(1)  Except as otherwise required in Subsections 3.11.4., 3.11.5., 3.11.6., and 3.11.7. or otherwise exempted in Sentences (2) and (3), Class A pools and Class B pools shall be designed and constructed to comply with Sentences (2) to (25).

(2)  Where a Class B pool is constructed for use solely in conjunction with a club, child care facility, day camp or establishment or institution for the care of persons who are infirm, aged or in custodial care, the pool shall be exempt from the requirements of Clause (9)(a) and Sentences (13) and (14).

(3)  Where a Class B pool is constructed for use solely in conjunction with an establishment or institution for the treatment of persons who are disabled or ill, the pool shall be exempt from the requirements of Sentences (6) and (7), Clause (9)(a) and Sentences (13) and (14).

(4)  A public pool shall be constructed to have a water depth of not less than 750 mm except for,

(a)	a modified pool,

(b)	a wave action pool,

(c)	a pool for therapeutic use,

(d)	a beach entry ramp, and

(e)	a pool described in Sentence 3.11.5.1.(1).

(5)  The beach entry ramp permitted in Clause (4)(d) shall be protected with permanent barriers between 900 mm to 1 200 mm along the pool deck to prevent entry into the pool until the minimum water pool depth is 750 mm.

(6)  Except for a modified pool, a wave action pool and a pool used exclusively for scuba diving, the slope of the bottom of any portion of a public pool shall not exceed,

(a)	8% where the water depth is 1 350 mm or less,

(b)	33% where the water depth is more than 1 350 mm and less than 2 000 mm, and

(c)	50% where the water depth is 2 000 mm or more.

(7)  Except for a modified pool and wave action pool, where the slope of any portion of the bottom of a public pool is more than 8%, the walls of the pool shall be equipped with recessed fittings to which a safety line supported by buoys can be attached across the surface of the water and the recessed fittings shall be installed at a horizontal distance of at least 300 mm measured from the vertical projection of the top of the slope in the direction of the shallow end of the pool.

(8)  Except for a modified pool, wave action pool and a pool described in Sentence 3.11.5.1.(1), the side and end walls of a public pool shall be vertical from the top of the walls to within 150 mm of the bottom except at steps or recessed ladders or in water depths of 1 350 mm or more.

(9)  Except for a modified pool and wave action pool and except as provided in Sentence (11), a public pool shall be surrounded by a hard-surfaced pool deck that shall,

(a)	except for a pool described in Sentence 3.11.5.1.(1), be not less than 1 800 mm wide and provide at least 900 mm width of clear passage,

(i)	behind any diving board and its supporting structure, and

(ii)	between any column piercing the deck and the edge of the pool or between the column and outer perimeter of the pool deck,

(b)	in the case of an outdoor pool, be sloped away from the pool to waste drains or to adjacent lower ground at a slope of between 2% and 4%, and

(c)	in the case of an indoor pool, be impervious and sloped away from the pool to waste drains at a slope of between 1% and 4%.

(10)  Where a public pool is constructed with a ledge, the ledge shall,

(a)	be placed only in parts of the pool where the water depth is 1 350 mm or more,

(b)	be not more than 200 mm wide,

(c)	be at least 1 000 mm below the water surface,

(d)	where located on the side of the pool, be gradually tapered towards the shallow end of the pool in such a manner as to prevent a harmful obstruction, and

(e)	have a band of contrasting colour along the entire juncture of the side and top of the ledge.

(11)  Notwithstanding Sentences (12) to (16), where a public pool is constructed on any level surface with walls rising above that surface and has a constant water depth not exceeding 1 100 mm and a water surface area not exceeding 100 m2, the pool deck may be an elevated platform surrounding the pool if it has,

(a)	an unobstructed width of not less than 900 mm,

(b)	a height of at least 75 mm above grade or pavement elevation,

(c)	6 mm wide openings for drainage, and

(d)	a non-slip surface that is capable of being kept clean and disinfected.

(12)  Except for a modified pool and wave action pool, where a pool deck projects over the water surface, the projection shall not exceed 50 mm.

(13)  Except for a modified pool and wave action pool, the pool deck shall be separated from any adjacent spectator area or gallery and from any spectator access to such area or gallery by a gate or other barrier.

(14)  Except for a modified pool and wave action pool, the perimeter of the pool deck shall be clearly delineated by painted lines or other means where any area contiguous to the pool deck may be confused with the deck.

(15)  Perimeter drainage shall be provided where necessary to prevent surface run-off from draining onto the pool deck.

(16)  Except for a modified pool, one or more hose bibs shall be installed near the perimeter of the pool deck in locations convenient for flushing the pool deck.

(17)  Except for a modified pool and wave action pool, where access to the pool enclosure is over any surface that is not subject to regular cleaning and sanitizing, a foot spray to wash feet by means of a spray running freely to waste shall be provided at each such access.

(18)  Except for a modified pool and wave action pool, at least one ladder or set of steps shall be provided in both the deep and shallow areas of a public pool for entry into and egress from the pool water.

(19)  The pool deck, the submerged parts of a public pool, the walls or partitions adjacent to a pool deck and the pavement or floor adjacent to a pool deck shall have surfaces that permit thorough cleaning.

(20)  Except for markings for safety or competition purposes, submerged surfaces in public pools shall be finished white or light in colour.

(21)  Except in a modified pool, a black disc 150 mm in diameter on a white background shall be affixed to the bottom of a public pool within the area of its greatest depth.

(22)  A public pool shall be equipped with lockable doors or other barriers capable of preventing public access to the pool deck.

(23)  Except for a modified pool, wave action pool or a pool installed at a recreational camp, a Class A pool shall be provided with,

(a)	where the water surface area is greater than 150 m2 but not greater than 230 m2, at least one lifeguard control station, and

(b)	where the water surface area is greater than 230 m2, at least two lifeguard control stations.

(24)  Except for a modified pool, every public pool shall display on the deck clearly marked figures, not less than 100 mm high, that set out,

(a)	the water depths indicating the deep points, the breaks between gentle and steep bottom slopes and the shallow points,

(b)	the words SHALLOW AREA at one or more appropriate locations, and

(c)	where the water depth exceeds 2 500 mm, the words DEEP AREA at one or more appropriate locations.

(25)  Except for a modified pool and a pool to which Sentence 3.11.5.1.(4) applies, every public pool having a maximum water depth of 2 500 mm or less shall display a warning notice posted in a location clearly visible to divers on which is printed in letters at least 150 mm high, the words CAUTION — AVOID DEEP DIVES or SHALLOW WATER — NO DIVING.

(26)  Except where no space is provided between ladder treads and the pool wall, the space between the pool wall and submerged portions of any treads of a ladder for entry into and egress from the water shall be not more than 150 mm and not less than 75 mm.

3.11.4.  Public Pools Equipped with Diving Boards or Diving Platforms

3.11.4.1.  Diving Boards or Platforms

(1)  No diving board or diving platform shall be installed in a public pool unless the requirements of Sentences (5) to (17) are met but the requirements for a diving platform do not apply to a starting platform.

(2)  No diving board or diving platform shall be installed in a modified pool or a wave action pool.

(3)  Where a public pool is equipped with a diving board or a diving platform, the board or platform shall have a non-slip surface.

(4)  Where a diving board or a diving platform in a public pool is more than 600 mmm above the water surface, the board or platform shall be equipped with one or more adjacent handrails.

(5)  Where a public pool is equipped with a diving board or a diving platform not more than 3 m in height above the water surface, the pool shall be designed and constructed in conformance with Sentences (6) to (15).

(6)  The depth of water in the area directly below a horizontal semi-circle in front of a diving board or diving platform having a radius of 3 m measured from any point on the front end of the board or platform shall not be less than,

(a)	2 750 mm, where a board is 600 mm or less in height above the water surface,

(b)	3 m, where a board or platform is greater than 600 mm but not more than 1 000 mm in height above the water surface, and

(c)	3.65 m, where a board or platform is greater than 1 000 mm but not more than 3 m in height above the water surface.

(7)  Except as permitted in Sentence (8), the water depth in a public pool shall be at least 1 350 mm at the horizontal arc having a radius of 9 m measured from any point on the front end of the diving board or diving platform and intersecting the vertical projections of the walls of the pool.

(8)  Where a Class B pool is equipped with a diving board 600 mm or less in height above the water,

(a)	the water depth shall be at least 1 350 mm at the horizontal arc having a radius of 7.5 m measured from any point on the front end of the diving board, and

(b)	a warning notice, on which is printed in letters at least 150 mm high, the words DANGER — AVOID DEEP OR LONG DIVES, shall be posted in a location clearly visible to divers.

(9)  The slope of the bottom of a public pool having a diving board or diving platform shall not change by more than 17% where the water depth is less than the applicable depth set out in Sentence (6) and greater than the depth set out in Sentence (7) or (8), as applicable.

(10)  The horizontal distance between the vertical projection of the centre line of a diving board or diving platform and the vertical projection of the centre line of another board or platform shall be at least 2 750 mm.

(11)  The horizontal distance between the centre line of a diving board or diving platform and the vertical projection of the closest side or any ledge on the closest side of a public pool shall be at least,

(a)	3 m, where a diving board or diving platform is 1 000 mm or less in height above the water surface, and

(b)	3.6 m, where a diving board or diving platform is greater than 1 000 mm in height above the water surface.

(12)  A diving board or a diving platform 600 mm or less in height above the water surface shall project over the water a horizontal distance of at least 900 mm from the vertical projection of a pool wall under it.

(13)  A diving board greater than 600 mm in height above the water surface shall project over the water a horizontal distance of at least 1 500 mm from the vertical projection of the pool wall under it.

(14)  A diving platform greater than 600 mm in height above the water surface shall project a horizontal distance of at least 1 200 mm from the vertical projection of the pool wall under it.

(15)  The space above a diving board or diving platform shall be unobstructed and shall consist of at least,

(a)	a space having a width of 2 500 mm on each side of the centre line of the board or platform, a length equal to the sum of the horizontal distance the board or platform projects over the water plus 3 m, and a height of,

(i)	3.65 m above a diving board 3.65 m or less in length,

(ii)	5 m above a diving board greater than 3.65 m in length, or

(iii)	3 m above a diving platform, and

(b)	the space below the planes originating from the front and sides of the uppermost horizontal plane of the space determined under Clause (a) and sloping downwards at 30° from the horizontal.

(16)  A diving board or diving platform greater in height than 3 m above the water surface shall be equipped with a gate, barrier or other device capable of preventing access to the diving board or diving platform.

(17)  Where a public pool is to be equipped with diving boards or diving platforms greater than 3 m in height above the water surface, the design of the diving boards or diving platforms and the corresponding water depths and clearances shall be in accordance with the “Rules and Laws Governing Swimming, Diving, Water Polo and Synchronized Swimming” published by FINA.

3.11.5.  Ramps into Public Pools in Group B, Division 2 or 3, Major Occupancies

3.11.5.1.  Ramps into Pools

(1)  Notwithstanding Sentences 3.11.3.1.(4) and (7) and Clause 3.11.3.1.(9)(a), where a public pool is constructed in a building containing a Group B, Division 2 or 3, major occupancy, and has a water depth not exceeding 1 500 mm and a water surface area not exceeding 100 m2, the pool deck contiguous to not more than 50 per cent of the total perimeter of the pool may be replaced by one or more ramps that will permit a bather seated in a wheelchair to enter the water with or without the wheelchair.

(2)  Where a public pool has one or more ramps as described in Sentence (1), the pool shall be designed and constructed to comply with Sentences (3) to (8).

(3)  A ramp referred to in Sentence (1) shall have,

(a)	a handrail having a height between 800 mm and 900 mm along each side of the ramp and running parallel to the slope of the ramp,

(b)	a width of at least 1 100 mm,

(c)	a curb or other means to prevent a wheelchair from falling off the side of the ramp,

(d)	surface finishes capable of being kept clean, sanitary and free from slipperiness, and

(e)	a landing at the bottom at least 1 500 mm in length and the same width as the ramp.

(4)  Notwithstanding Sentence 3.11.3.1.(25), a warning notice, on which is printed in letters at least 150 mm high, the words CAUTION — NO DIVING, shall be posted conspicuously on each wall or fence line enclosing the pool.

(5)  There shall be a curb along the perimeter of the pool except at steps, ladders and ramp entrances.

(6)  The curb shall have,

(a)	a height of 50 mm,

(b)	rounded edges,

(c)	a coved base, and

(d)	a raised nosing at the top to serve as a fingerhold for a bather in the water.

(7)  Where a ramp that is not submerged is adjacent to the pool wall and is used for access to the water, the pool shall be constructed so that,

(a)	the landing at the bottom of the ramp is at least 450 mm but not more than 550 mm below the top of the wall separating the ramp from the pool,

(b)	the landing is equipped with a floor drain at its lowest point,

(c)	the top of the wall between the pool and the ramp is at least 250 mm and not more than 300 mm in width,

(d)	the pool deck is capable of accommodating a movable barrier separating the deck from the ramp,

(e)	the water depth at the landing shall be accurately and clearly marked at the landing in figures at least 100 mm high on the top of the wall separating the pool from the ramp, and

(f)	the ramp shall have a slope not exceeding 8%.

(8)  Where a submerged ramp is adjacent to the pool wall and is used for access to the water, the pool shall be constructed so that,

(a)	the water depth at the bottom of the ramp is at least 600 mm and not greater than 900 mm,

(b)	a hard-surfaced area that is at least 750 mm wide is contiguous to the entire length of the part of the submerged ramp that pierces any part of the deck,

(c)	the area described in Clause (b) is capable of accommodating a movable barrier that separates the area from the deck,

(d)	the finishes in submerged portions of the ramps and curbs are different in colour or shade from each other and from that of the pool walls and bottom, and

(e)	the submerged ramp has a slope not exceeding 11%.

3.11.6.  Modified Pools

3.11.6.1.  Construction Requirements

(1)  A modified pool is exempt from Sentences (4) to (9), (12), (13), (14), (16), (17), (18), (21), (23), (24) and (25) of Article 3.11.3.1. and Sentence 3.11.8.1.(12).

(2)  A modified pool shall be designed and constructed to comply with Sentences (3) to (9).

(3)  A modified pool and its pool deck shall be constructed of hard-surfaced material that permits thorough cleaning.

(4)  The slope of the bottom of any portion of a modified pool shall not exceed 8%.

(5)  The depth of the water in any portion of a modified pool shall not be more than 1 800 mm.

(6)  A modified pool shall be surrounded on all sides by a hard-surfaced pool deck that shall,

(a)	be at least 3 m wide,

(b)	have a continuous crest surrounding the pool at least 100 mm above the pool water surface, and

(c)	be sloped to shed water from the crest to the outer perimeter of the pool deck.

(7)  A modified pool shall be provided with two or more drain fittings covered with protective grilles with openings having an aggregate area of at least 10 times the internal cross-sectional area of the outlet pipe or pipes connected to the recirculation system that is capable of completely draining the pool.

(8)  Provision shall be made for lifeguard control stations adjacent to the edge of the water at intervals of not more than 60 m.

(9)  The bottom of a modified pool shall be marked with continuous black contour lines,

(a)	150 mm wide located where the water depth is 600 mm and

(b)	300 mm wide located where the water depth is 1 200 mm.

3.11.7.  Wave Action Pools

3.11.7.1.  Construction Requirements

(1)  A wave action pool is exempt from Sentences (4) to (9), (12) to (14), (17), (18) and (23) of Article 3.11.3.1. and Sentence 3.11.8.1.(12).

(2)  A wave action pool shall be designed and constructed to comply with Sentences (3) to (11).

(3)  The slope of the bottom of any portion of a wave action pool,

(a)	shall not exceed 8% where the still water depth is less than 1 000 mm, and

(b)	shall not exceed 11% where the still water depth is 1 000 mm or more.

(4)  The walls of a wave action pool shall be vertical from the water surface to within 150 mm of the bottom.

(5)  There shall be a hard-surfaced pool deck at least 3 m wide immediately adjacent to the pool wall at the shallow end of the pool and at least 1 500 mm wide immediately adjacent to all walls of the pool.

(6)  Provision shall be made for two or more lifeguard control stations on each side of the pool deck adjacent to which the still water depth exceeds 1 000 mm.

(7)  Sets of steps or ladders recessed into pool side walls and having continuous vertical grab bars on each side of them shall be located at intervals of not more than 7.5 m along portions of the pool where the still water depth exceeds 1 000 mm, except that no steps or ladders shall be located within 3 m of the corners at the deep end of the pool.

(8)  Except at recessed steps or ladders, the pool deck along each side of a wave action pool adjacent to which the water depth is 2 300 mm or less shall be equipped with a barrier supported by posts or a wall that,

(a)	is 1 000 mm in height,

(b)	is located 1 000 mm or less from the side of the pool, and

(c)	has warning notices affixed to the barrier or wall at intervals not exceeding 7.5 m signifying clearly that jumping and diving are prohibited along the sides of the pool.

(9)  Skimming devices shall be designed and suitably located to remove surface film when no waves are induced in a wave action pool.

(10)  A system capable of deactivating the wave-making equipment shall be installed with readily accessible push buttons located on the pool deck not more than 30 m apart, adjacent to each side and the deep end of the pool.

(11)  A wave action pool shall be equipped with a first-aid room located within 50 m of the pool.

3.11.8.  Recirculation for Public Pools

3.11.8.1.  Recirculation Systems

(1)  Every public pool shall be equipped with a recirculation system.

(2)  For the purposes of this Subsection, the water in a public pool and its recirculation system shall be deemed not to be potable water.

(3)  The water in a public pool and its recirculation system shall be separated from the potable water supply and from the sewer or drainage system into which it drains by air gaps or other devices that prevent,

(a)	the water in the pool or its recirculation system from flowing back into the potable water supply, and

(b)	the water in the sewer or drainage system from flowing back into the pool or its recirculation system.

(4)  The recirculation system of a public pool shall be designed, constructed and equipped to comply with Sentences (5) to (20).

(5)  The recirculation system of a public pool shall be capable of filtering, disinfecting and passing through the pool each day a volume of water of at least,

(a)	in the case of a Class A pool, other than a modified pool or a wave action pool, six times the total water volume of the pool,

(b)	in the case of a Class B pool, other than a wave action pool, four times the total water volume of the pool,

(c)	in the case of a modified pool, three times the total water volume of the pool, and

(d)	in the case of a wave action pool, six times the total water volume of the pool.

(6)  A recirculation system shall be equipped with a flow meter registering the rate of water flow.

(7)  All pools shall be provided with automatic make-up water devices and provided with water meters to register the volume of all make-up water added to a public pool or its recirculation system.

(8)  Equipment shall be installed to continuously disinfect the water in a public pool by means of,

(a)	a chlorination or hypochlorination system provided with a chemical controller for regulating the dosage of chlorine and capable of providing not less than,

(i)	in the case of an outdoor pool, other than a wave action pool, 300 g of chlorine per day per 10 000 L of total pool capacity,

(ii)	in the case of an indoor pool, other than a wave action pool, 200 g of chlorine per day per 10 000 L of total pool capacity,

(iii)	in the case of an outdoor wave action pool, 1 200 g of chlorine per day per 10 000 L of total pool capacity, and

(iv)	in the case of an indoor wave action pool, 800 g of chlorine per day per 10 000 L of total pool capacity, or

(b)	a bromination system capable of maintaining in the pool water a total bromine residual of 3 mg/L.

(9)  Chlorination equipment for a public pool shall contain a mechanism whereby the chlorine feed shall automatically terminate whenever the recirculation system ceases to supply clean water to the pool.

(10)  All exposed potable water piping and chlorine piping within a public pool water treatment service room shall be colour coded by means of,

(a)	painting the entire outer surface of the piping, or

(b)	coloured bands at least 25 mm in width that are spaced along the piping at intervals of not more than 1 200 mm.

(11)  The colour coding referred to in Sentence (10) shall be yellow for chlorine and green for potable water.

(12)  Except for a modified pool and wave action pool, a public pool shall be equipped with overflow gutters or surface skimmers connected to the recirculation system that are capable of removing surface film from the surface of the water and withdrawing each day and discharging to the waste drains up to 15 per cent of the total volume of pool water.

(13)  A public pool shall be equipped with clean water inlets arranged in conjunction with surface skimmers or overflow gutters to provide uniform distribution and circulation of clean water.

(14)  Except as permitted in Sentence (19), all fittings at or below the water surface that allow water and/or air to be passed to or from the public pool shall,

(a)	have a maximum opening of 7 mm in one direction, and

(b)	be securely held in place by corrosion resistance fastening that require a tool for removal and are galvanically compatible with the fittings and grilles or covers.

(15)  Except as provided in Sentence 3.11.6.1.(7) for a modified pool, all fittings below the water surface that provide suction or gravity flow in a public pool shall,

(a)	be provided with a minimum of two suction or gravity outlets interconnected to a full size manifold, and

(b)	be separated by a clear distance of not less than 1 200 mm.

(16)  Except as provided in Sentence 3.11.6.1.(7) for a modified pool, water in all public pools shall be capable of being emptied through the pool drains in twelve hours or less.

(17)  Except as provided in Sentence 3.11.6.1.(7) for a modified pool, openings in suction or gravity fittings shall,

(a)	be such that the flow of water does not exceed 0.45 m/s and the velocity is calculated assuming all possible sources of suction flow are present at one time, and

(b)	be such that every suction fitting located within 1 000 mm of the water surface, except for skimmers and gutter fittings, contain openings with a minimum aggregate area of 0.2 m2.

(18)  Except for skimmers and gutters, all submerged suction and gravity fittings shall be clearly and permanently marked with a 50 mm wide band in a contrasting colour.

(19)  Fittings returning water and/or air to the pool tank that are located within 300 mm of the water surface are permitted to have openings with one dimension more than 7 mm but shall contain no openings more than 25 mm in diameter.

(20)  Submerged skimmer equalizer fittings and vacuum fittings are not permitted in public pools.

3.11.9.  Dressing Rooms, Locker Facilities and Plumbing Facilities for all Public Pools

3.11.9.1.  Dressing Rooms and Sanitary Facilities

(1)  Except as otherwise permitted in Sentences (2) and (3), every public pool shall be equipped with dressing rooms, locker rooms, shower heads, water closets, urinals, lavatories and drinking fountains that shall be designed, constructed and equipped to comply with Sentences (4) to (14).

(2)  Where a Class A pool is installed on the premises of a recreational camp, dressing rooms, locker rooms, shower heads, water closets, urinals, lavatories and drinking fountains are not required if,

(a)	dressing, water closet and shower facilities are conveniently available for bathers elsewhere on the premises, and

(b)	foot sprays are provided in accordance with Sentence 3.11.3.1.(17).

(3)  Where a Class B pool is installed, dressing rooms, locker rooms, shower heads, lavatories, water closets, drinking fountains and urinals are not required if,

(a)	dressing, water closet and shower facilities are conveniently available elsewhere on the premises for bathers when the pool is open for use, and

(b)	foot sprays are provided in accordance with Sentence 3.11.3.1.(17).

(4)  The minimum number of water closets, urinals and lavatories shall be determined from Article 3.7.4.3. and Table 3.7.4.3.C. for an occupant load based on,

(a)	the formula in Sentence 3.1.17.3.(1) for all public pools, except a wave action pool, or

(b)	the formula in Sentence 3.1.17.3.(2) for a wave action pool.

(5)  A minimum of one shower head shall be provided for every 40 bathers.

(6)  Where dressing and locker rooms, water closets and urinals are provided in conjunction with a public pool, they shall be located in such a manner that bathers, after using them, shall pass through or by a shower area to reach the pool deck.

(7)  All shower heads shall be supplied with potable water at a pressure of at least 140 kPa.

(8)  The shower water system shall have one or more tempering devices capable of being adjusted to ensure that water supplied to shower heads does not exceed 40°C.

(9)  Floors in washrooms, shower areas and passageways used by bathers shall slope to waste drains at not less than 1% and shall be of hard surfaced materials that do not become slippery when wet.

(10)  Joints between floors and walls shall be coved in areas described in Sentence (9) and in dressing and locker rooms.

(11)  Hose bibs shall be provided in safe locations convenient for flushing down the walls and floors in washrooms, shower areas and passageways used by bathers.

(12)  Partitions or walls shall be provided to ensure privacy of dressing rooms, washrooms and shower areas.

(13)  The bottom of interior partitions in dressing rooms and washrooms shall be between 250 mm and 350 mm above the floor.

(14)  Dressing and locker room floors shall have non-slip surfaces that permit convenient and thorough cleaning and disinfecting.

3.11.10.  Emergency Provisions for All Public Pools

3.11.10.1.  Lighting and Emergency Provisions

(1)  Except as provided in Sentences (2) and (3), rooms and spaces used by the public in conjunction with a public pool shall be capable of illumination to levels in compliance with Subsection 3.2.7.

(2)  Dressing rooms, locker rooms, shower rooms, washrooms and passageways shall have an illumination level of at least 200 lx at floor level.

(3)  An indoor pool or an outdoor pool that is intended to be open for use after sundown shall be equipped with a lighting system,

(a)	that will maintain at any point on the pool deck and on the pool water surface an illumination level of at least,

(i)	200 lx in the case of an indoor pool, and

(ii)	100 lx in the case of an outdoor pool, and

(b)	that makes the underwater areas of the pool clearly visible from any point on the pool deck.

(4)  An outdoor pool that is intended to be open for use after sundown and an indoor pool shall be equipped with an independent emergency lighting system that automatically operates whenever the normal electrical power supply to a public pool lighting system fails.

(5)  The independent emergency lighting system required in Sentence (4) shall be capable of illuminating the pool deck, washroom, shower, locker areas, pool water surface and all means of egress to a level of at least 10 lx.

(6)  An emergency power supply for the emergency lighting system required in Sentence (4) shall comply with Sentences 3.2.7.4.(1) and 3.2.7.7.(1) and Article 3.2.7.5.

(7)  An emergency telephone directly connected to an emergency service or to the local telephone utility shall be installed adjacent to the pool deck of every Class A pool.

(8)  A telephone accessible for emergency use shall be installed for every Class B pool within 30 m of the pool.

(9)  Every wave action pool shall have a public address system that shall be clearly audible in all portions of the pool.

(10)  Every wave action pool shall have a communication system for the use of persons engaged in supervision or operation of the pool that shall be interconnected with each lifeguard control station, the first-aid room and the bather admission control centre.

(11)  The public address system and the communication system described in Sentences (9) and (10) shall be interconnected.

(12)  All recirculating pumps used in a public pool shall be capable of being deactivated by an emergency stop button clearly labelled and located at,

(a)	a Class A pool beside the telephone that is required in Sentence (7), and

(b)	a Class B pool on the deck area.

(13)  The emergency stop button in Sentence (12) shall when used activate an audible and a visual signal located by the emergency stop.

(14)  An emergency sign containing the words IN THE EVENT OF AN EMERGENCY PUSH EMERGENCY STOP BUTTON AND USE EMERGENCY PHONE, AUDIBLE AND VISUAL SIGNAL WILL ACTIVATE shall be in letters at least 25 mm high with a 5 mm stroke and posted above the emergency stop button.

3.11.11.  Service Rooms and Storage for All Public Pools

3.11.11.1.  Service Rooms and Storage Facilities

(1)  In addition to the requirements of this Subsection, service rooms shall comply with the requirements of Sentences 3.6.2.1.(5), 3.6.2.1.(7) and 3.6.2.1.(8) and Articles 3.5.3.3. and 3.6.2.2.

(2)  Where compressed chlorine gas is used as a pool water disinfectant, the cylinders or containers of gas shall be located in a service room that,

(a)	except as provided in Sentences 3.1.9.4.(3) to (8), is separated from the remainder of the building by a 1 h fire separation that is substantially gas tight,

(b)	is designed for the sole purpose of containing all installed pressurized chlorine gas apparatus and piping and storing all chlorine gas containers or chlorine gas cylinders that are individually secured against toppling,

(c)	is located at or above ground level,

(d)	is provided with an exit door opening to the outdoors,

(e)	has screened openings to the outdoors with at least one opening located within 150 mm from the floor and at least one opening located within 150 mm from the ceiling, each opening being 2% of the area of the floor,

(f)	is equipped with emergency mechanical ventilation capable of producing at least 30 air changes per hour, taking suction at a maximum of 900 mm above the floor level and discharging at least 2 500 mm above ground level directly to the outdoors, and

(g)	contains a platform weigh scale of at least 135 kg capacity for each chlorine cylinder in use.

(3)  Storage facilities shall be provided for the safe storage of all chemicals required in pool operations.

(4)  The storage facilities shall be ventilated and shall be equipped with a water hose connection and a floor drain.

(5)  Service rooms and storage facilities, including rooms and facilities that contain electrical or mechanical equipment or chemicals or chemical feeders, shall be equipped with a secure locking device.

Section 3.12.  Public Spas

3.12.1.  General

3.12.1.1.  Application

(1)  This Section applies to the design and construction of site-assembled public spas and factory-built public spas.

(2)  If material alterations to a public spa or the equipment installed in a public spa affect the bottom slope, the water volume or the capacity of the water circulation system, the adversely affected portions shall comply with the requirements of this Division.

(3)  Except as provided in Sentence (4), if material alterations or repairs concern any pool fitting that passes water or air, or both, in or out of the pool tank, the affected fitting shall comply with Sentences 3.11.8.1.(20) and 3.12.4.1.(4) to (10).

(4)  If the material alterations or repairs concern a fitting cover or grille, the affected fitting cover or grille shall comply with Sentences 3.12.4.1.(7) to (10).

(5)  For the purposes of this Section, every reference to a public pool or a recirculation system in a definition in Article 1.4.1.2. of Division A, or a Sentence or Clause in Section 3.11. that is made applicable to public spas by this Section, shall be deemed to be a reference to a public spa or water circulation system, respectively.

3.12.2.  Public Spa and Deck Design and Construction Requirements

3.12.2.1.  Construction Requirements

(1)  In addition to the requirements of this Subsection, public spas shall comply with the requirements of Sentences 3.11.3.1.(13) to (17), (19), (20) and (22) and Clause 3.11.3.1.(24)(a).

(2)  A public spa shall be constructed to have a water depth of not more than 1 200 mm.

(3)  The slope of the bottom of any portion of a public spa shall not exceed 8%.

(4)  A public spa shall be surrounded by a hard-surfaced pool deck that,

(a)	shall have a minimum clear deck space of not less than 1.8 m at the main entrance point,

(b)	shall have a clear deck space of 900 mm on all sides, except as required by Clause (a) and permitted by Sentence (5),

(c)	shall be sloped away from the pool to waste drains or to adjacent lower ground at a slope of between 2% and 4%, in the case of an outdoor public spa, and

(d)	shall be impervious and sloped away from the pool to waste drains at a slope of between 1% and 4%, in the case of an indoor public spa.

(5)  One section of the hard-surfaced pool deck that does not exceed 25% of the perimeter of the public spa may have a minimum clear deck space of not more than 300 mm if,

(a)	the public spa has an area less than 6 m2, and

(b)	the public spa has no interior dimension more than 2.5 m.

(6)  The maximum depth of water to a seat or bench in a public spa shall be 600 mm.

(7)  If a set of steps is provided for entry into and egress from the public spa water, the steps,

(a)	shall be equipped with a handrail,

(b)	shall have a non-slip surface, and

(c)	shall have a band of contrasting colour along the entire juncture of the side and top of the edges.

(8)  Every public spa shall be provided with dressing rooms, water closets and shower facilities that are conveniently available on the premises.

(9)  Except where no space is provided between ladder treads and the spa wall, the space between the spa wall and submerged portions of any treads of a ladder for entry into and egress from the water shall be not more than 150 mm and not less than 75 mm.

3.12.3.  Ramps into Public Spas

3.12.3.1.  Ramps into Spas

(1)  Not more than 50% of the total perimeter of a public spa may be replaced by one or more ramps that permit a bather seated in a wheelchair to enter the water with or without the wheelchair.

(2)  If a public spa has one or more ramps described in Sentence (1), the public spa shall comply with Sentences 3.11.5.1.(1) to (3) and (5) to (8).

3.12.4.  Water Circulation for Public Spas

3.12.4.1.  Water Circulation Systems

(1)  In addition to the requirements of this Subsection, the water circulation system of a public spa shall comply with the requirements of Sentences 3.11.8.1.(2), (3), (6), (7), (9), (10), (11), (13) and (20).

(2)  A public spa shall be equipped with a water circulation system that is capable of filtering, disinfecting and passing the public spa water through the public spa with a turnover period of not more than,

(a)	30 minutes for a public spa with a volume of water that exceeds 6 m3,

(b)	20 minutes for a public spa with a volume of water that exceeds 4 m3 but does not exceed 6 m3, or

(c)	15 minutes for a public spa with a volume of water that does not exceed 4 m3.

(3)  If cartridge-type filters are used for a public spa, the filters shall be a surface-type that is designed for a maximum flow rate of 0.27 L/s/m2 effective filter area.

(4)  Except as provided in Sentence (6), every circulation system in a public spa shall be served by a minimum of two suction or gravity outlets,

(a)	that are interconnected to a full size manifold, and

(b)	except as provided in Sentence (5), that are separated by a clear distance of not less than 900 mm.

(5)  If compliance with Clause (4) (b) is impracticable because of dimensional restrictions at the bottom of the public spa, the outlets may be located on two different planes of the public spa if,

(a)	at least one of the outlets through which the public spa can be emptied to a full-size manifold is located on the bottom of the public spa, and

(b)	the bottom of all outlets, other than skimmers, are not more than 75 mm from the floor of the public spa.

(6)  A circulation system in a factory-built public spa may be served by a built-in suction or gravity outlet with multiple openings that are connected to a full-size manifold.

(7)  All fittings at or below the water surface that allow water or air or both to be passed to or from the public spa shall be securely held in place by corrosion resistant fastening that requires a tool for removal and is galvanically compatible with the fittings and grilles or covers.

(8)  Except as provided in Sentence (9), all suction or gravity fittings installed at or below the water line of a public spa shall,

(a)	have a maximum opening of 7 mm in one direction, and

(b)	be designed so that the flow of water through the openings does not exceed 0.45 m/s.

(9)  Sentence (8) does not apply to suction and gravity outlets that are equipped with anti-entrapment covers that comply with the requirements of ANSI/ASME A112.19.8M, “Suction Fittings for Use in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Whirlpool Bathtub Appliances”.

(10)  The calculation of water velocities for the purposes of Clause (8)(b) and Sentences (11) and (12) and the calculation of water flow rates for the purposes of Sentence (9) shall be based on the assumption that all possible sources of suction flow are present at the same time.

(11)  The water velocity in a suction pipe shall not exceed 1.8 m/s.

(12)  The water velocity in a pressure pipe shall not exceed,

(a)	3.0 m/s for plastic piping, and

(b)	1.8 m/s for copper piping.

(13)  Every suction system that serves a public spa shall be equipped with a vacuum relief mechanism that shall include,

(a)	a vacuum release system,

(b)	a vacuum limit system, or

(c)	other engineered systems that are designed, constructed and installed to conform to good engineering practice appropriate to the circumstances.

(14)  Equipment shall be installed to continuously disinfect the water in a public spa by means of a chlorination, hypochlorination or bromination system that is capable of regulating the dosage of chlorine or bromine.

(15)  If a two-speed pump is utilized for a public spa, the filter and heater shall be sized to accommodate the maximum pump output, without exceeding the manufacturer’s design flow rate of the filter element or heater and without by-passing the filter element.

(16)  A public spa equipped with hydro-massage jet fittings shall be provided with a timing device,

(a)	that controls the period of operation of the jet pump, and

(b)	that is placed in a location where the user must exit the public spa to reset the timer.

(17)  A public spa water heater shall be equipped with an upper limit cut-off device,

(a)	that is independent of the normal public spa water temperature thermostat, and

(b)	that limits the maximum water temperature of the public spa to 40°C.

(18)  A public spa shall be equipped with a water circulation system that is capable of both completely and partially draining and refilling the public spa water.

3.12.5.  Emergency Provisions for All Public Spas

3.12.5.1.  Lighting and Emergency Provisions

(1)  In addition to the requirements of this Subsection, public spas shall comply with the requirements of Sentences 3.11.10.1.(1) to (6).

(2)  An emergency telephone directly connected to an emergency service or to the local telephone utility shall be installed within 30 m of the public spa.

(3)  All pumps used in a public spa shall be capable of being deactivated by an emergency stop button that is clearly labelled and located within the immediate vicinity of the public spa.

(4)  The emergency stop button required in Sentence (3),

(a)	shall be a switch separate from the public spa’s timing device,

(b)	shall activate an audible and a visual signal when used, and

(c)	shall have an emergency sign conforming to Sentence 3.11.10.1.(14).

(5)  If a public spa and public pool are located in the same room or space, the emergency stop buttons required in Sentences (3) and 3.11.10.1.(12) shall deactivate all pumps serving the public spa and public pool.

3.12.6.  Service Rooms and Storage for All Public Spas

3.12.6.1.  Service Rooms and Storage Facilities

(1)  Service rooms and storage facilities for all public spas shall comply with the requirements of Article 3.11.11.1.

Section 3.13.  Rapid Transit Stations

3.13.1.  Scope and Definitions

3.13.1.1.  Scope

(1)  Except as provided in this Section the requirements in this Division apply to rapid transit stations.

3.13.1.2.  Definitions

(1)  In this Section:

Ancillary space means the rooms or spaces in the station used only by the transit agency to house or contain operating, maintenance or support equipment and functions, but does not include booths and kiosks used by the transit agency or service rooms.

Central supervising station means the operations centre where the transit agency controls and co-ordinates the system-wide movement of passengers and vehicles and from which communication is maintained with supervisory and operating personnel of the transit agency and with participating agencies when required.

Crush load means the total of the seating capacity and the standing capacity of a car where,

(a)	the seating capacity is the number of seats in a car, and

(b)	the standing capacity is 0.2 m2 per person for the standing area which is measured 300 mm in front of the seats.

Egress capacity means the number of people able to travel from or through a type of egress facility in a specified period of time.

Entraining load means the number of passengers boarding the train at a station.

Fare-paid area means that portion of a rapid transit station to which access is gained by a pass or by paying a fare.

Fare-paid area control means the point where passengers enter or leave the fare-paid area.

Link load means the number of passengers on board the train(s) travelling between two stations.

Maximum calculated train load means the crush load per car multiplied by the maximum number of cars per train in the peak period.

Peak direction means, for each route, the direction of train travel having the largest passenger flow volume based on the sum of the incoming link load plus the entraining load per peak hour.

Protected route means that portion of a means of egress that starts at the point where passengers would not be vulnerable to exposure from a train fire and that leads to the exterior of the station or through an exit to an adjacent building.

Public area means the public circulation areas in a rapid transit station providing pedestrian access to and from trains.

Rapid transit station means a building or part of a building used for the purpose of loading and unloading passengers of a rapid transit system but does not include open air shelters at street level.

Rapid transit system means an electrified transportation system, utilizing guidance methods involving positive mechanical contact with the fixed way operating on a right-of-way for the mass movement of passengers.

3.13.2.  Construction Requirements

3.13.2.1.  Requirements for Stations

(1)  Except as provided in this Subsection, the requirements in Subsections 3.2.1. and 3.2.2. do not apply to a rapid transit station.

(2)  The requirements in Sentence (3) shall apply to,

(a)	a rapid transit station erected entirely below the adjoining finished ground level, and

(b)	the underground portion of a rapid transit station.

(3)  Except as permitted in Sentence (4), an underground station or an underground portion of a station in Sentence (2) shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations having a fire-resistance rating not less than 2 h,

(b)	roof assemblies below ground level, shall have a fire-resistance rating not less than 2 h, but a fire-resistance rating is not required where steel tunnel liners are left in place to form part of the assembly and the tunnel liners are in direct contact with soil, and

(c)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(4)  An interior stair extending to street level is permitted to be protected by a combustible roof.

(5)  Where a rapid transit station is erected above and below the adjoining finished ground level, the above ground portion of the station shall be of noncombustible construction and shall conform to the requirements in Sentence (10).

(6)  Where a rapid transit station is erected entirely above the adjoining finished ground level and is a stand-alone building, the station shall be of noncombustible construction and shall conform to the requirements in Sentence (11).

(7)  Openings for stairways and escalators used by passengers are permitted to penetrate the fire separations required in Sentences (2) to (6).

(8)  Elevator shafts are permitted to penetrate the fire separations required in Sentences (2) to (6) provided they are enclosed by,

(a)	a fire separation having a fire-resistance rating not less than 1 h, or

(b)	wired glass assemblies conforming to Supplementary Standard SB-2.

(9)  Openings for other than stairways, escalators or elevators are permitted to penetrate the fire separations required in Sentences (2) to (6) provided the openings are protected by a closure having a fire-protection rating not less than 45 min.

(10)  The building shall be of noncombustible construction and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

(b)	mezzanines shall have a fire-resistance rating not less 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(11)  Except as provided in Sentence (12), the building shall be of noncombustible construction, and,

(a)	floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

(b)	mezzanines shall have a fire-resistance rating not less than 1 h,

(c)	roof assemblies shall have a fire-resistance rating not less than 1 h, and

(d)	all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

(12)  A building classified as Group A, Division 2 occupancy that is not more than 1 storey in building height, and in which the building area is not more than 3 200 m2 if not sprinklered, or 6 400 m2 if sprinklered, is permitted to be constructed with a roof of heavy timber construction and have columns of heavy timber construction.

3.13.3.  Safety Requirements Within Stations

3.13.3.1.  Application

(1)  Except as provided in this Subsection and Subsection 3.13.4., the requirements in Subsections 3.3.1. and 3.6.2. apply to a rapid transit station.

(2)  A door in a fire separation is permitted to be equipped with pivot hinges in conformance with Table 2-8A of NFPA 80, “Fire Doors and Windows”.

(3)  The requirements in Subsection 3.4.4. for fire separation of exits do not apply in a rapid transit station.

(4)  Except as provided in Sentence (5), the requirements in Sentence 3.4.6.15.(1) for doors to be readily opened from the inside apply to required exit doors in a rapid transit station.

(5)  Where a group of two or more doors serves as a single exit facility, only one door in the group is required to comply with Sentence 3.4.6.15.(1).

(6)  A door that is required to be readily opened in Sentence (4) or (5) shall have a sign attached to it that,

(a)	displays the words EMERGENCY EXIT with the letters not less than 25 mm high, and

(b)	is visible from the exit approach.

3.13.3.2.  Booths and Kiosks

(1)  Booths and kiosks that are not more than 20 m2 in area and are used only by the transit agency for fare collection, dissemination of information or similar non-mercantile occupancies shall be of noncombustible construction and are not required to be separated from the remainder of the floor area by a fire separation.

(2)  Booths and kiosks that are more than 20 m2 in area and are used only by the transit agency for fare collection, dissemination of information or similar non-mercantile occupancies shall be,

(a)	sprinklered, and

(b)	separated from the remainder of the floor area by a fire separation of noncombustible construction that is not required to have a fire-resistance rating.

(3)  A door acting as a closure in the fire separation in Sentence (2) is not required to be equipped with a self-closing device.

3.13.3.3.  Service Rooms and Ancillary Spaces

(1)  An ancillary space in a rapid transit station shall be separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 1 h.

(2)  Except as provided in Sentence (3), a door opening from a service room onto a means of egress in a rapid transit station shall be located not less than 5 m from an escalator balustrade and from the top and bottom riser of a flight of stairs used as a means of egress from the rapid transit station.

(3)  The requirements in Sentence (2) do not apply where,

(a)	the service room is sprinklered, or

(b)	there is a vestibule between the service room and the means of egress.

(4)  Where a door from a service room opens onto a means of egress less than 5 m wide,

(a)	the service room shall be sprinklered, or

(b)	there shall be a vestibule between the service room and the means of egress.

3.13.3.4.  Leased Areas

(1)  All leased areas within a rapid transit station shall be,

(a)	sprinklered, and

(b)	separated from the remainder of the floor area by a fire separation of noncombustible construction that is not required to have a fire-resistance rating.

(2)  A door acting as a closure in the fire separation in Clause (1)(b) is not required to be equipped with a self-closing device.

(3)  Where leased areas are located on opposite sides of a means of egress, the width of the means of egress shall not be reduced to less than 5 m.

(4)  Except as provided in Sentence (5), where the leased area on any floor level exceeds 15% of the public area on that level, the public area shall be sprinklered.

(5)  In a rapid transit station that is erected entirely above the adjoining finished ground level and is a stand-alone building, where the leased area on any floor level exceeds 20% of the public area on that level, the public area shall be sprinklered.

(6)  In determining the leased area in Sentences (4) and (5), it is not necessary to include a leased area that is separated from the public area by a fire separation having a fire-resistance rating not less than,

(a)	2 h where the leased area contains a mercantile or medium hazard industrial occupancy, or

(b)	1 h where the leased area contains any other occupancy.

(7)  A leased area is permitted on a platform level provided it is,

(a)	located not less than 5 m from the platform edge,

(b)	located not less than 5 m from an egress facility, and

(c)	not located in a dead end portion of the platform.

3.13.3.5.  Vehicle Terminal

(1)  Where an enclosed terminal serves vehicles powered by combustible fuels, and the terminal has direct access to a rapid transit station,

(a)	the terminal shall be sprinklered, and

(b)	the terminal shall be separated from the rapid transit station,

(i)	by a fire separation having a fire-resistance rating not less than 1 h, or

(ii)	by wired glass assemblies conforming to Supplementary Standard SB-2 with wired glass doors equipped with self-closing devices.

(2)  Doors in the fire separation or in the wired glass assembly in Clause (1)(b) are not required to have latches where close spaced sprinkler protection is provided on the station side.

3.13.3.6.  Access to Adjacent Building

(1)  Where an access is provided between a rapid transit station and an adjacent building, the station and the building shall be separated by a fire separation having a fire-resistance rating not less than 2 h.

(2)  The access in Sentence (1) shall be through a vestibule that is separated from the station and from the building,

(a)	by a fire separation having a fire-resistance rating not less than 1 h, or

(b)	by wired glass assemblies conforming to Supplementary Standard SB-2 with wired glass doors equipped with self-closing devices.

(3)  The vestibule doors in Sentence (2),

(a)	are not required to be equipped with latches, and

(b)	shall swing in the direction of travel from the rapid transit station.

(4)  Close spaced sprinkler protection shall be provided on each side of all vestibule doors.

(5)  The vestibule shall not contain an occupancy.

(6)  Where an access is provided between a rapid transit station and an adjacent building, and the building is regulated by the provisions of Subsection 3.2.6. or 3.2.8., these provisions are not required in the rapid transit station.

3.13.3.7.  Emergency Lighting

(1)  Emergency lighting shall be provided to average levels not less than 10 lx at floor or tread level in public areas in a rapid transit station.

(2)  An emergency power supply conforming to Subsection 3.2.7. shall be provided to maintain the emergency lighting required in Sentence (1) for a period of 30 min after a power failure.

3.13.4.  Means of Egress

3.13.4.1.  Occupant Load

(1)  The occupant load for public areas within a rapid transit station shall be,

(a)	determined in conformance with this Subsection, and

(b)	based on peak hour patronage as projected for design of the transit system.

(2)  The platform occupant load for each platform in a rapid transit station shall be the greater of the a.m. or p.m. peak period loads calculated in accordance with Sentences (3) to (5).

(3)  The a.m. and the p.m. peak period occupant loads for each platform shall be based on the simultaneous evacuation of the entraining load and the link load for that platform.

(4)  The entraining load for each platform shall be the sum of the entraining loads for each track serving that platform and the entraining load for each track shall be based on the entraining load per train headway multiplied by,

(a)	a factor of 1.3 to account for surges, and

(b)	in the peak direction for each route, an additional factor of 2 to account for a missed headway.

(5)  The link load for each platform shall be the sum of the link loads for each track serving that platform and, except as provided in Sentence (6), the link load for each track shall be based on the link load per train headway multiplied by,

(a)	a factor of 1.3 to account for surges, and

(b)	in the peak direction for each route, an additional factor of 2 to account for a missed headway.

(6)  The maximum link load at each track shall be the maximum calculated train load.

3.13.4.2.  General Requirements

(1)  Except as provided in Sentence (2), escalators conforming to the requirements of Sentences 3.13.4.5.(3) and 3.13.4.6.(1) shall be acceptable as part of a required means of egress in a rapid transit station.

(2)  Escalators forming part of a required means of egress shall not comprise more than one half of the required egress capacity from any one level.

(3)  Horizontal exits conforming to Sentence (4) may provide all of the required egress capacity from a rapid transit station.

(4)  Horizontal exits to any one building shall not comprise more than one half of the required egress capacity from any area within a rapid transit station.

(5)  A protected route shall be provided with emergency ventilation conforming to Subsection 3.13.7.

(6)  In an aboveground unenclosed station, the protected route is permitted to begin at the point of leaving the platform.

(7)  In an enclosed or underground station, the protection for the protected route shall consist of,

(a)	a fire separation having a fire-resistance rating not less than 1 h,

(b)	construction having a fire-resistance rating not less than 1 h, or

(c)	wired glass assemblies conforming to Supplementary Standard SB-2.

3.13.4.3.  Number and Location of Means of Egress

(1)  Each platform in a rapid transit station shall be served by no fewer than 2 means of egress that are independent of and remote from each other from the platform to the exterior of the station.

(2)  Where a continuous level walking surface is provided between two adjacent platforms, they may be considered as one platform for the purpose of conforming to this Subsection.

(3)  At the platform level, the distance separating the egress facilities in Sentences (1) and (2) shall be the greater of one car length or 25 m.

(4)  Except as required in Sentence (1), two or more means of egress are permitted to converge in conformance with Sentence 3.13.4.4.(6).

(5)  Means of egress from platforms shall be located so that the travel time from the most remote point on a platform to a protected route does not exceed 4 min based on travel speeds of,

(a)	38 m/min for horizontal travel, and

(b)	21 m/min for vertical rise.

3.13.4.4.  Egress Capacity

(1)  For a rapid transit station, the required aggregate egress capacity from each platform shall be determined by dividing the platform occupant load determined in accordance with Sentences 3.13.4.1.(2) to (6) by the required platform clearance time determined in accordance with Sentence (3).

(2)  Where 2 platforms are considered as 1 platform as provided in Sentence 3.13.4.3.(2), the required egress capacity for each platform shall be determined separately.

(3)  The required platform clearance time shall be 4 min less the travel time between the platform and the entry into the protected route based on travel speeds of,

(a)	38 m/min for horizontal travel, and

(b)	21 m/min or vertical rise.

(4)  For each means of egress, the required egress capacity at the platform shall be maintained for the entire length of the means of egress.

(5)  Except as provided in Sentence (6), where 2 or more means of egress converge, the required egress capacity beyond that point shall be cumulative.

(6)  The egress capacity in Sentence (5) need not be cumulative after converging where it can be shown that the platform clearance time in Sentence (3) is not exceeded.

3.13.4.5.  Width of Means of Egress

(1)  Except as otherwise required in this Subsection, the required width of means of egress serving platforms in a rapid transit station shall be determined based on,

(a)	the required egress capacity determined in conformance with Article 3.13.4.4., and

(b)	the pedestrian flow rate for the type of means of egress facility listed in Table 3.13.4.5.

(2)  In calculating the required width of corridors and ramps with a grade of less than 4%, 300 mm at each sidewall shall be added to the width determined based on required egress capacity.

(3)  In calculating the required width of egress routes, one escalator at each level in a rapid transit station shall be deemed to be out of service and not available for egress purposes.

Table 3.13.4.5.
Pedestrian Flow Rates

Forming Part of Sentence 3.13.4.5.(1)

| Column 1 | Column 2 | Column 3 |
| --- | --- | --- |
| Type of Egress Facility | Flow Rate, pedestrians per minute | Flow Rate, pedestrians per minute per metre width |
| Platforms | N/A | 80 |
| Corridors | N/A | 80 |
| Doorways | N/A | 80 |
| Gates | N/A | 80 |
| Ramps not more than 4% | N/A | 80 |
| Ramps more than 4 % | N/A | 55(1) |
| Stairs | N/A | 55(1) |
| Escalators moving in direction of egress travel, nominal width |  |  |
| : 1 200 mm | 100 | N/A |
| : 800 mm | 80 | N/A |
| : 600 mm | 60 | N/A |
| Turnstiles, height of bar |  |  |
| : not more than 900 mm | 45 | N/A |
| : more than 900 mm | 25 | N/A |

Note to Table 3.13.4.5.:

(1) Flow rate is applied vertically.

(4)  Except as provided in Sentence (5), the minimum width of means of egress facilities serving platforms shall be,

(a)	1 750 mm for corridors and ramps,

(b)	1 750 mm for stairs,

(c)	430 mm for turnstiles,

(d)	500 mm for fare collection gates,

(e)	600 mm nominal width for escalators, and

(f)	900 mm for a door leaf.

(5)  A second means of egress as required by Sentence 3.13.4.3.(1) is permitted to be not less than 1 100 mm wide.

(6)  The minimum width of platforms shall be,

(a)	3.2 m for side platforms, and

(b)	6.4 m for island platforms.

(7)  The minimum unobstructed width of platforms measured from the platform edge shall be 2.5 m.

3.13.4.6.  Egress Facilities

(1)  Escalators forming part of a required means of egress shall,

(a)	where equipped to run reverse to the direction of egress travel, be capable of being stopped remotely and locally, and

(b)	have a vertical rise not more than 12 m between floors or landings.

(2)  Where electrically operated gates or turnstiles used for fare collection are intended to be used as part of a required means of egress from a rapid transit station, provision shall be made to release the gates or turnstiles in accordance with Sentence (4) to allow them to operate freely in the direction of egress travel.

(3)  Where locked doors that prevent entry into a fare-paid area are to be used as part of a required means of egress from a rapid transit station, provision shall be made to release the doors in accordance with Sentence (4) to allow them to operate freely in the direction of egress travel.

(4)  The release device required in Sentences (2) and (3) shall be installed as an ancillary device to the fire alarm system and shall release immediately,

(a)	upon activation of the fire alarm signal,

(b)	in the event of a power failure or ground fault, or

(c)	upon actuation of a manually operated switch accessible to authorized personnel and located in,

(i)	a fare collector’s booth or kiosk at the station, or

(ii)	the central supervising station.

(5)  After release, the gates or turnstiles in Sentence (2) or the doors in Sentence (3) shall be capable of reactivation only by manual actuation of the switch in Clause (4)(c).

3.13.5.  Fire Safety Provisions

3.13.5.1.  Fire Alarm System

(1)  Except as provided in this Subsection, a fire alarm system conforming to Subsection 3.2.4. shall be installed in a rapid transit station.

3.13.5.2.  Exceptions

(1)  Manual pull stations need not be installed in a rapid transit station.

(2)  Audible signal appliances need not be installed in a rapid transit station.

3.13.5.3.  Fire Detectors

(1)  Except where the area is sprinklered, fire detectors shall be installed in every service room, ancillary space, leased space, booth and kiosk.

3.13.5.4.  Central Supervising Station

(1)  Each rapid transit station shall be monitored by a central supervising station conforming to CAN/ULC-S561, “Installation and Services for Fire Signal Receiving Centres and Systems”.

3.13.5.5.  Annunciators

(1)  An annunciator shall be installed,

(a)	in a location that is readily accessible to fire fighters entering the building, and

(b)	in the rapid transit station,

(i)	in a designated collector’s booth, or

(ii)	within viewing distance of a designated collector’s booth.

3.13.5.6.  Annunciator Indication

(1)  All fire alarm, fire detectors, valve switches and water flow indicator signals when activated in a rapid transit station shall be indicated on the annunciator at the station.

(2)  The annunciator at a rapid transit station shall be monitored simultaneously at the central supervising station.

(3)  Where a means of egress from a rapid transit station leads through an adjoining building, any alarm signal originating in the building within two storeys above a connection to the station shall,

(a)	be indicated on the rapid transit station annunciator, and

(b)	cause a message to flash a warning on a sign located in conformance with Sentence (4), that the means of egress shall not be used as an exit from the station.

(4)  A sign required in Clause (3)(b) shall be located,

(a)	at the doors from the rapid transit station to the adjoining building, and

(b)	in the means of egress to the adjoining building, at the last point where there is a choice of direction to travel to at least one other exit.

3.13.5.7.  Emergency Power

(1)  An emergency power supply conforming to Article 3.2.7.8. shall be provided for the fire alarm system.

3.13.5.8.  Communication Systems

(1)  In a rapid transit station, a public address system shall be installed and shall include loudspeakers that,

(a)	can be operated from the central supervising station,

(b)	can be operated from the rapid transit station in which they are located, and

(c)	designed and located so that voice messages can be heard intelligibly throughout the public area in a rapid transit station.

(2)  A 2-way communication system shall be installed in each rapid transit station with telephones located at,

(a)	the collector’s booth, and

(b)	at each end of each platform.

(3)  The telephones in Sentence (2) shall be provided with connections to the central supervising station.

3.13.5.9.  Emergency Reporting Devices

(1)  Emergency reporting devices shall be located on passenger platforms and throughout a rapid transit station such that the distance of travel from any point in the public area to such a device is not more than 90 m.

(2)  The emergency reporting devices required in Sentence (1) are permitted to be public telephones with an emergency no charge capability and their location shall be plainly indicated by appropriate signs.

3.13.5.10.  Sprinkler Systems

(1)  Sprinkler systems shall conform with the requirements of Articles 3.2.5.13 to 3.2.5.16.

(2)  In addition to the requirements of Subsection 3.13.3. the steel truss enclosure of an escalator shall be sprinklered.

(3)  There shall be identification on a fire department connection for a sprinkler system in a rapid transit station to indicate that the connection is part of the station system.

3.13.5.11.  Standpipe and Hose Systems

(1)  A standpipe and hose system conforming to the requirements of Subsection 3.2.9. shall be installed in a rapid transit station, except as otherwise required or permitted in this Article.

(2)  Where a rapid transit station includes more than one standpipe riser there shall be a cross-connection pipe having a diameter not less than 100 mm between each standpipe riser so that supplying of water through any fire department connection will furnish water throughout each riser.

(3)  There shall be identification on a fire department connection for a standpipe system in a rapid transit station to indicate that the connection is part of the station system.

(4)  Hose stations shall be located so that every portion of the rapid transit station can be reached by a hose stream and is within 3 m of a hose nozzle when the hose is extended.

(5)  In addition to the requirements in Sentence (4), hose stations shall be located in each tunnel not more than 20 m from the end of the platform.

(6)  The requirement for hose rack and fire hose in Sentence 3.2.9.4.(2) does not apply in a rapid transit station.

(7)  Each hose station shall have a 38 mm hose connection and a 65 mm hose connection.

(8)  All supply piping shall have a diameter not less than 100 mm.

3.13.6.  Required Sanitary Facilities

3.13.6.1.  Application

(1)  Except as provided in this Subsection, Subsection 3.7.4. applies to a rapid transit station.

3.13.6.2.  Washrooms Required

(1)  Except as provided in Sentences (2) and (3), a washroom for each sex, containing at least 1 water closet and 1 lavatory, shall be provided in each rapid transit station for use by employees.

(2)  Where the number of employees in a rapid transit station is not more than 5, a washroom containing 1 water closet and 1 lavatory is permitted to be used by both sexes provided the door to the room can be locked from the inside.

(3)  Where a rapid transit station is not staffed during operating hours, a washroom is not required in the station.

(4)  In each rapid transit station located at the end of a line, a washroom for each sex, containing no fewer than 3 water closets and 2 lavatories, shall be provided for use by the public.

3.13.7.  Emergency Ventilation

3.13.7.1.  Application

(1)  Every rapid transit station shall be provided with an emergency ventilation system conforming to NFPA 130, “Fixed Guideway Transit Systems”.

3.13.8.  Barrier-Free Design

3.13.8.1.  Application

(1)  Except as provided in this Subsection, the requirements in Section 3.8. apply to rapid transit stations.

(2)  At least one barrier-free path of travel shall be provided from an entrance described in Article 3.8.1.2.,

(a)	into the fare-paid area, and

(b)	to each platform.

3.13.8.2.  Exception

(1)  Where an elevator is used to comply with the requirements of Article 3.3.1.7., the provisions of Clause 3.3.1.7.(1)(a) do not apply where the elevator system complies with Article 3.13.8.3.

3.13.8.3.  Elevator Requirements

(1)  Except as provided in Sentence (2), the elevator in Article 3.13.8.2. shall be capable of providing transportation from each platform to an entrance described in Article 3.8.1.2.

(2)  Where it is necessary to change elevators to reach the entrance described in Sentence (1), the elevator system shall be designed so that not more than one change of elevator is required between,

(a)	a platform and a fare-paid area control, and

(b)	the fare-paid area control and the entrance.

3.13.8.4.  Emergency Operation of Elevators

(1)  Manual emergency recall operation shall be provided for all elevators.

(2)  Key-operated switches for emergency recall described in Sentence (1) shall be provided and shall be located on the outside of each elevator shaft at the level of the fare-paid area control.

(3)  In-car emergency service switches shall be provided in all elevator cars.

(4)  Keys to operate the switches required in Sentences (2) and (3) shall be located at,

(a)	the annunciator required in Clause 3.13.5.5.(1)(a), and

(b)	the collector’s booth designated in Clause 3.13.5.5.(1)(b).

3.13.8.5.  Washrooms Required to be Barrier-Free

(1)  A barrier-free path of travel shall be provided to the washrooms required in Article 3.13.6.2.

(2)  Where a washroom required in Sentence 3.13.6.2.(1) contains only 1 water closet and 1 lavatory, the washroom shall be designed in conformance with the requirements in Article 3.8.3.12.

(3)  Where a washroom required in Sentence 3.13.6.2.(1) contains more than 1 water closet, the washroom shall be designed in conformance with the requirements in Articles 3.8.3.8. to 3.8.3.11.

(4)  The washroom required in Sentence 3.13.6.2.(2) shall be designed in conformance with the requirements in Article 3.8.3.12.

(5)  The washrooms required in Sentence 3.13.6.2.(4) shall be designed in conformance with the requirements in Articles 3.8.3.8. to 3.8.3.11.

Section 3.14.  Tents and Air-Supported Structures

3.14.1.  Tents

3.14.1.1.  Application

(1)  Except as provided in this Subsection, tents are exempted from complying with the requirements of this Division.

3.14.1.2.  General

(1)  Except as provided in Sentence (2), the requirements of this Subsection shall apply to all tents.

(2)  Articles 3.14.1.4., 3.14.1.5., 3.14.1.6. and 3.14.1.9. apply to tents that,

(a)	do not exceed 225 m2 in ground area,

(b)	do not exceed 225 m2 in aggregate ground area and are closer than 3 m apart,

(c)	do not contain bleachers, and

(d)	are not enclosed with sidewalls.

3.14.1.3.  Means of Egress

(1)  Except as provided in Sentences (2) and (3), tents shall conform to Sections 3.3. and 3.4.

(2)  A tent need not conform to Article 3.4.6.11. except where swing type doors are provided.

(3)  Where the area between adjacent tents or a tent and the property line is used as a means of egress, the minimum width between stake lines shall be the width necessary for means of egress, but not less than 3 m.

3.14.1.4.  Clearance to Other Structures

(1)  Tents shall not be erected closer than 3 m to the property line.

(2)  Except as provided in Sentences (3), (4) and (5), tents shall not be erected closer than 3 m to other tents or structures on the same property.

(3)  A walkway between a building and a tent occupied by the public is permitted provided,

(a)	the tent is not closer than 3 m from the building, and

(b)	the walkway conforms to Article 3.2.3.19.

(4)  Tents not occupied by the public need not be separated from one another, and are permitted to be erected less than 3 m from other structures on the same property, where such closer spacing does not create a hazard to the public.

(5)  Tents located on fair grounds or similar open spaces, need not be separated from one another provided such closer spacing does not create a hazard to the public.

3.14.1.5.  Clearances to Flammable Material

(1)  The ground enclosed by a tent and for not less than 3 m outside of such structure shall be cleared of all flammable or combustible material or vegetation that will carry fire.

3.14.1.6.  Flame Resistance

(1)  Every tent, and tarpaulins, decorative materials, fabrics and films used in connection with tents, shall be certified to CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films”, or NFPA 701 “Fire Tests for Flame-Resistant Textiles and Films”.

3.14.1.7.  Bleachers

(1)  Where bleachers are provided in tents, they shall be designed in conformance with Articles 3.3.2.8., 3.3.2.10. and Subsection 4.1.5.

3.14.1.8.  Sanitary Facilities

(1)  Except as provided in Sentence (3), the minimum number of water closets for tents shall be determined in accordance with Table 3.7.4.3.E.

(2)  Article 3.7.4.16. applies to sanitary facilities in Sentence (1).

(3)  Sanitary privies, chemical closets or other means for the disposal of human waste may be provided in lieu of toilet fixtures.

3.14.1.9.  Provision for Fire Fighting

(1)  Access shall be provided to all tents for the purpose of fire fighting.

3.14.2.  Air-Supported Structures

3.14.2.1.  Application

(1)  Except as provided in this Subsection, the requirements of this Division apply to air-supported structures.

3.14.2.2.  General

(1)  Air-supported structures shall not be used for Groups B, C, or Group F, Division 1 major occupancies or for classrooms.

(2)  Except where no fire separation is required between major occupancies, air-supported structures shall contain not more than one major occupancy.

(3)  Except as provided in Sentence (5), air-supported structures are exempt from complying with Articles 3.2.2.20. to 3.2.2.83., except for maximum building size.

(4)  Air-supported structures may be designed with interior walls, mezzanines, or similar construction.

(5)  Interior construction contained within air-supported structures must meet the construction requirements of Articles 3.2.2.20. to 3.2.2.83.

3.14.2.3.  Spatial Separation

(1)  Except as provided in Sentences (2), (3) and (4), air-supported structures shall not be erected closer than 3 m to other structures on the same property or to the property line.

(2)  Air-supported structures not occupied by the public need not be separated from one another, and are permitted to be erected closer than 3 m from other structures on the same property where such closer spacing does not create a hazard to the building occupants or the public.

(3)  Except as provided in Sentence (4), an air-supported structure is permitted to be attached to another building provided the building to which it is attached,

(a)	conforms to the requirements of other Parts of this Division based on the total building areas of the air-supported structure and the attached building,

(b)	is sprinklered, and

(c)	is separated from the air-supported structure by a fire separation having a fire-resistance rating of not less than 1 h.

(4)  An air-supported structure is permitted to be attached to another building provided the building to which it is attached,

(a)	has a building area not more than 200 m2,

(b)	conforms to the requirements of other Parts of the Code based on the building area of the attached building, and

(c)	is sprinklered or separated from the air-supported structure by a fire separation having a fire-resistance rating of not less than 1 h.

3.14.2.4.  Clearances to Flammable Material

(1)  The ground enclosed by an air-supported structure and for not less than 3 m outside of such structure shall be clear of all flammable or combustible material or vegetation that will carry fire.

3.14.2.5.  Flame Resistance

(1)  Air-supported structures shall be constructed of material conforming to CAN/ULC-S109, “Flame Tests of Flame-Resistant Fabrics and Films”, or NFPA 701, “Fire Tests for Flame-Resistant Textiles and Films”.

(2)  Materials for fabrics used in connection with air-supported structures are exempt from compliance with the requirements for flame-spread ratings for interior finishes in Subsection 3.1.13.

3.14.2.6.  Emergency Air Supply

(1)  An air-supported structure designed for an assembly occupancy with an occupant load of more than 200 persons shall have either an automatic emergency engine-generator set capable of powering one blower continuously for 4 h, or a supplementary blower powered by an automatic internal combustion engine.

Section 3.15.  Signs

3.15.1.  Scope

3.15.1.1.  Application

(1)  Except as provided otherwise in Article 3.15.1.2. this Section shall apply to the erection of all signs.

3.15.1.2.  Exceptions

(1)  The following signs shall not be subject to the provisions of this Section,

(a)	signs for regulating traffic or similar devices, legal notices or warnings at railroad crossings,

(b)	signs in display windows including writing, representation, painting or lettering directly on the surface of any window or door, or other signs not affixed to the building interior,

(c)	small signs displayed for the direction of the public including signs that identify rest rooms, freight entrances and such other similar directional signs,

(d)	signs painted directly on a building, and

(e)	incidental signs or other signs subject to municipal approval.

3.15.2.  Alterations

3.15.2.1.  Exceptions for Alterations

(1)  The changing of movable parts of signs that are designed for changes, or the repainting of display matter shall not be deemed to be alterations.

3.15.3.  Structural Requirements

3.15.3.1.  Structural Design

(1)  Except as provided in this Section, all sign structures shall be designed in accordance with Part 4.

3.15.4.  Plastic Sign Facing Materials

3.15.4.1.  Combustible Sign Faces

(1)  Plastic materials used in the construction of sign faces shall,

(a)	have an average burning rate not greater than 65 mm/min in sheets 1.5 mm thick when tested in accordance with ASTM D635, “Rate of Burning and/or Extent and Time of Burning of Self-supporting Plastics in a Horizontal Position”,

(b)	have an average burning rate not greater than 140 mm/min when tested in accordance with ASTM D568, “Rate of Burning and/or Extent and Time of Burning of Flexible Plastics in a Vertical Position”, and

(c)	have a measurement of material thickness in accordance with Method B-Machinists’ Micrometer Without Ratchet of ASTM D374, “Thickness of Solid Electrical Insulation”.

(2)  Except as provided in Sentence (3), where the exterior cladding of a wall is required to be noncombustible, a plastic sign face or a group of contiguous plastic sign faces may be placed over such cladding provided each such sign face or group of contiguous sign faces,

(a)	does not exceed 30% of the wall area of the storey on which it is installed,

(b)	does not exceed 15 m2 in area or 1 200 mm in height at each storey, and

(c)	when located above the first storey, is vertically separated from other plastic sign faces by 1 200 mm of noncombustible construction unless separated by a horizontal noncombustible projection such as a canopy, extending the full width of, and projecting at least 900 mm beyond the exterior sign face.

(3)  Where a plastic exterior sign is mounted as a face on a metal sign box that is at least 200 mm in depth, the requirements of Sentence (2) need not apply provided the sign box is mounted on a noncombustible exterior wall.

(4)  Notwithstanding the requirements of Sentence (5), the plastic portion of an interior sign placed over or forming part of an interior wall surface in corridors, covered or enclosed walkways at or above grade in buildings shall,

(a)	not exceed 15% of the wall area in, or over which it may be installed,

(b)	be supported by a device that will not detrimentally affect the fire-resistance rating of the interior wall to which it is attached or of which it may form a part, and encase the edges of the plastic sign face in metal,

(c)	not be positioned or sized in such a manner that it is less than 600 mm from the vertical line separating two adjacent premises,

(d)	be placed so that there is at least 600 mm vertical separation of noncombustible material between the top of the plastic sign surface and the ceiling surface,

(e)	be permitted to have an increase of 100% in area required in Clause (a) and a decrease of 50% of the separation distances required in Clauses (c) and (d) if the area is sprinklered, and

(f)	have a flame-spreading rating not more than 250.

(5)  Signs in exits and underground walkways shall have a flame-spread rating not more than 25.

3.15.5.  Location Restrictions

3.15.5.1.  Obstructions not Permitted

(1)  No sign shall be located so as to obstruct openings required for light and ventilation, any required means of egress or required access for fire fighting in accordance with Sentence 3.2.5.3.(2).

3.15.5.2.  Clearance for Exterior Signs

(1)  No exterior sign shall be erected overhanging a sidewalk or other pedestrian walkway unless the vertical distance, measured from the bottom of the overhanging portion of the sign to the surface of the sidewalk, is at least 2 400 mm.

(2)  Except as provided in Sentence (3), no sign face shall be erected within 600 mm of the vehicular travelled portion of a private lane or roadway, or of a motor vehicle parking area unless the minimum vertical distance between grade and the bottom of the overhanging sign face is at least 4.25 m.

(3)  Where the height of all vehicles using any private road or parking area is permanently restricted, the vertical distance in Sentence (2) may be reduced to the amount of the actual height restriction, for as long as the said height restriction is in existence on the premises.

Section 3.16.  Shelf and Rack Storage Systems

3.16.1.  Scope

3.16.1.1.  Application

(1)  The requirements of this Section apply to a shelf and rack storage system.

(2)  The requirements of Subsection 3.2.8. do not apply to a shelf and rack storage system conforming to this Section.

(3)  The requirements of Subsection 3.16.2. apply to a shelf and rack storage system for the storage of Class I, II, III and IV commodities as defined in NFPA 13, “Installation of Sprinkler Systems”.

(4)  The requirements of Subsection 3.16.3. apply to a shelf and rack storage system for the storage of Group A, B and C plastics and rubber tires as defined in NFPA 13, “Installation of Sprinkler Systems”.

3.16.1.2.  General

(1)  A shelf and rack storage system shall not be designed for production, manufacturing, assembling, disassembling or ancillary administrative functions.

(2)  A shelf and rack storage system may be designed for the storage, accessing, retrieval, packing and distribution of commodities.

(3)  A high hazard industrial occupancy shall not contain a shelf and rack storage system.

(4)  Except as required by Sentence 3.16.3.2.(3), a shelf and rack storage system shall not exceed 24 m in height.

3.16.1.3.  Construction

(1)  All structural components of a shelf and rack storage system, including posts, beams, decks, walkways, connections and their supports such as concrete slabs and foundations, shall be designed in accordance with Part 4.

(2)  Except as required by Sentence 3.16.3.2.(2), platform and walkway levels shall be of,

(a)	solid construction consisting of steel plate or steel roof decking with a top substrate that forms a serviceable floor area, or

(b)	open construction consisting of steel grating or open steel floor planking.

(3)  Guards and toe-boards shall be provided in accordance with Articles 3.3.1.17. and 3.3.5.8.

(4)  Every platform or walkway level shall be provided with fire extinguishers installed in conformance with the provisions of Part 6 of the Fire Code made under the Fire Protection and Prevention Act, 1997.

3.16.1.4.  Signs

(1)  A permanent sign shall be posted in a conspicuous location to indicate the maximum permissible design loads for each shelf and rack storage system.

(2)  Permanent signs shall be posted in conspicuous locations with,

(a)	the words NO SMOKING in black lettering not less than 50 mm high with a stroke not less than 12 mm on a yellow background, or

(b)	a non-smoking symbol having a size not less than 150 mm by 150 mm.

3.16.1.5.  Lighting

(1)  Walkways and platforms shall be equipped to provide illumination to an average level not less than 50 lx at floor or tread level and at angles and intersections at changes of level where there are stairs or ramps.

(2)  Emergency lighting on walkways, platforms, unenclosed egress stairs and exits providing means of egress shall conform to not less than,

(a)	the illumination level in Sentences 3.2.7.3.(2) and (3), and

(b)	the duration in Sentence 3.2.7.4.(1).

3.16.1.6.  Sprinkler System

(1)  An automatic sprinkler system conforming to this Article shall be installed in a floor area containing a shelf and rack storage system.

(2)  The automatic sprinkler system shall be designed, constructed, installed and tested in conformance with NFPA 13, “Installation of Sprinkler Systems” or the appropriate NFPA sprinkler standard for the most severe hazard to which the storage system is exposed.

(3)  Sprinkler protection shall be provided under all platforms and walkways.

(4)  Except where the platforms or walkways are of open construction, any openings for egress stairs shall be protected by non-combustible draft stops not less than 450 mm below the floors above.

(5)  The automatic sprinkler system shall be electrically supervised to indicate a trouble signal on the building fire alarm system annunciator or where the building does not have a fire alarm system, to notify the person controlling the operation of the building for each of the situations listed in Sentence 3.2.4.9.(2).

(6)  The automatic sprinkler system shall be designed to notify the fire department that a waterflow switch has been activated.

(7)  The notification to the person controlling the building and the fire department referred to in Sentences (5) and (6) shall be provided in accordance with Sentence 3.2.4.7.(4).

(8)  A permanent sign shall be posted, at or near the sprinkler control valve, containing,

(a)	the word NOTICE in contrasting letters,

(b)	a description of the commodity class as defined in NFPA 13, “Installation of Sprinkler Systems”, and

(c)	the sprinkler design criteria used for the shelf and rack storage system.

3.16.1.7.  Exits and Means of Egress

(1)  Except as permitted in Sentences (2) and (3), every walkway or platform level shall be provided with no fewer than two exits conforming to Section 3.4.

(2)  An access to exit from an elevated platform level may be provided by means of open unenclosed stairs serving,

(a)	not more than four platform levels, the highest of which shall be not more than 12 m above the main floor, where the shelf and rack storage system is intended for the storage of Class I, II, III and IV commodities, as defined in NFPA 13, “Installation of Sprinkler Systems”, and

(b)	not more than two platform levels, where the shelf and rack storage system is intended for the storage of Group A, B and C plastics and rubber tires, as defined in NFPA 13, “Installation of Sprinkler Systems”.

(3)  Any single platform or walkway in a shelf and rack storage system may be served by a single unenclosed stair leading to the platform or walkway level immediately below provided,

(a)	the platform or walkway does not exceed 200 m2 in area,

(b)	the travel distance on the platform or walkway to the level below, including the travel distance along the single unenclosed egress stair, does not exceed 25 m, and

(c)	the platform or walkway below is provided with two separate egress stairs or exits.

(4)  The maximum travel distance on an elevated platform to the ground floor level, including the travel distance along unenclosed stairs, shall not exceed 45 m.

(5)  The maximum travel distance on an elevated platform to an exit serving that platform shall not exceed 45 m.

(6)  Except as permitted in Sentence (7), the maximum travel distance from the bottom of an unenclosed stair to an exit along a main aisle on the ground floor level shall not exceed 45 m.

(7)  Where the travel distance in Sentence (6) exceeds 45 m,

(a)	an egress system serving the shelf and rack storage system shall be designed on the basis of a time-based egress analysis using the following criteria:

(i)	occupant egress speed of 1 m/sec shall be used for horizontal egress routes within the shelf and rack storage system,

(ii)	occupant egress speed of 0.6 m/sec shall be used for vertical egress routes within the shelf and rack storage system, measured on the diagonal along the nosing of the stairs,

(iii)	occupant egress speed of 1.3 m/sec shall be used for horizontal egress routes along a main aisle on the ground floor level,

(iv)	each lift-gate shall be accorded an egress time of 10 seconds,

(v)	each at-level conveyor cross-over shall be accorded a time of 5 seconds,

(vi)	a safety factor of 1.5 shall be used in calculating the total egress time

(b)	the total egress time shall be calculated using the following formula:

Total Egress Time = (Hp + Vp/0.6 + Hm/1.3 + 10Nlg + 5Nlc ) · 1.5 (in seconds)

where:

Hp =	horizontal travel distance on the shelf and rack storage system, in metres,

Vp =	vertical travel distance on the shelf and rack storage system, in metres,

Hm =	horizontal travel distance on the main floor, in metres,

Nlg =	number of lift gates in the means of egress,

Nlc =	number of at-level cross overs in the means of egress,

(c)	the total egress time from any point in the shelf and rack storage system shall be a maximum of 4 minutes,

(d)	a fire alarm and detection system conforming to Subsection 3.2.4. shall be installed in the building,

(e)	smoke detectors shall be provided under all solid decking and walkways,

(f)	clearly identified and easily accessible pull stations shall be provided at egress stairs, conveyor cross-overs or lift-gates located along egress paths, and

(g)	the occupant load on each level of the shelf and rack storage system shall not exceed 10 persons per egress stair.

(8)  A dead end aisle shall not exceed 9 m where the platform or walkway is provided with 2 or more egress facilities.

(9)  An aisle serving a shelf and rack storage system shall have a clear-aisle width of not less than 760 mm.

(10)  Conveyors, trolleys, tracks or any other similar mode of product transportation within the aisle or walkway shall not reduce the clear-aisle width required in Sentence (9).

(11)  Where exits are provided to comply with Sentence 3.4.2.5.(2), main aisles serving the shelf and rack storage system on the ground floor, leading from egress stairs directly to an exit, shall be clearly demarcated and have a minimum unobstructed, clear-aisle width of 2.4 m.

(12)  Where a lift-gate is incorporated along an egress route,

(a)	a maximum of two lift-gates may be within a single egress route,

(b)	each lift-gate shall be equipped with a positive lock when open, and

(c)	it shall be designed to automatically stop the conveyor belt that it serves when the lift-gate is open.

(13)  Where an at-level conveyor cross-over is incorporated along an egress route,

(a)	not more than two at-level conveyor cross-overs shall be within a single egress route,

(b)	handrails spaced not more than 1 m apart and parallel to the direction of egress shall be provided on both sides of the at-level cross-over,

(c)	flat, metal inserts shall be placed between each roller over the required egress width at each at-level conveyor cross-over to provide a walking surface,

(d)	at least two inserts not less than 100 mm wide shall be arranged symmetrically between the handrails serving the at-level cross-over,

(e)	inserts shall be sized to support loads specified in Part 4,

(f)	a clearly identified and easily accessible switch that will stop the conveyor shall be located at each at-level cross-over, and

(g)	stairs approaching at-level conveyor cross-overs shall be marked to indicate that they are readily identifiable as part of the egress route.

3.16.2.  Storage of Class I, II, III and IV Commodities

3.16.2.1.  Application

(1)  The requirements in this Subsection apply to a shelf and rack storage system intended for the storage of Class I, II, III and IV commodities as defined in NFPA 13, “Installation of Sprinkler Systems”.

3.16.2.2.  Construction

(1)  Where the height of a shelf and rack storage system, measured from the floor supporting the system to the topmost portion of the shelf, exceeds 18 m,

(a)	a fire alarm and detection system conforming to Subsection 3.2.4. shall be installed with,

(i)	pull stations located at all exit doors including exit doors serving elevated decks and walkways, and

(ii)	smoke detectors located, at the ceiling of all rooms and areas containing the shelf and rack storage system, within exit stair enclosures at the top, and at every third level of elevated deck or walkway, and

(b)	the fire alarm and detection system required by Clause (a), shall be designed to notify the fire department upon activation, and

(c)	the shelf and rack storage system shall be designed only for the storage of Class I, II and III commodities as defined in NFPA 13, “Installation of Sprinkler Systems”.

3.16.3.  Storage of Group A, B and C Plastics and Rubber Tires

3.16.3.1.  Application

(1)  The requirements in this Subsection apply to a shelf and rack storage system intended for the storage of Group A, B and C plastics and rubber tires as defined in NFPA 13, “Installation of Sprinkler Systems”.

3.16.3.2.  Construction

(1)  A shelf and rack storage system intended for the storage of rubber tires shall conform to the requirements to Subsection 3.3.1. “Indoor Tire Storage” of the Fire Code made under the Fire Protection and Prevention Act, 1997.

(2)  Platform and walkway levels shall not be of open construction.

(3)  A shelf and rack storage system shall not exceed 7 m in height.

Section 3.17.  Additional Requirements for Change of Use

3.17.1.  Scope

3.17.1.1.  Application

(1)  This Section applies where proposed construction in respect of an existing building will result in any of the following changes of use of all or part of the building:

(a)	a change of the major occupancy of all or part of a building that is designated with a “Y” in Table 1.3.1.4. of Division C,

(b)	a suite of a Group C major occupancy is converted into more than one suite of a Group C major occupancy,

(c)	a suite or part of a suite of a Group A, Division 2 or a Group A, Division 4 major occupancy is converted to a gaming premises,

(d)	a farm building or part of a farm building is changed to a major occupancy,

(e)	a building or part of a building is changed to a post-disaster building, or

(f)	the use of a building or part of a building is changed and the previous major occupancy of the building or part of the building cannot be determined.

(2)  For the purposes of this Section and Sentences 11.4.2.1.(1) and 11.4.2.5.(4), the changes of use set out in Clauses (1)(b) to (d) shall also be deemed to constitute a change in major occupancy.

(3)  The requirements of this Section are in addition to the requirements of other Parts of this Division as they apply to the proposed construction.

3.17.2.  Additional Construction

3.17.2.1.  Change of Use and Compensating Construction

(1)  Where proposed construction will result in a change of use described in Clauses 3.17.1.1.(1)(a) to (d), additional construction shall be required in order that the building or part of a building subject to the change of use conforms to the requirements of Subsection 3.2.6. and Sections 3.7., 3.11. and 3.12. as they apply to the new major occupancy that the building or part of a building is to support.

(2)  For the purposes of this Article, existing buildings shall be classified as to their construction and occupancy as provided for in Sentence 11.2.1.1.(1).

3.17.2.2.  Performance Level and Compensating Construction

(1)  The performance level of a building after construction shall not be less than the performance level of the building prior to construction.

(2)  For the purposes of Sentence (1), reduction of performance level shall be determined in accordance with Articles 11.4.2.1., 11.4.2.3. and 11.4.2.5.

(3)  Where proposed construction would reduce the performance level of an existing building, compensating construction shall be required in conformance with Articles 11.4.3.1., 11.4.3.2., 11.4.3.4. and 11.4.3.6.

(4)  Section 11.5. applies in respect of the requirements of Sentences 11.4.3.4.(1), (3) and (4).

O. Reg. 350/06, Division B, Part 3; O. Reg. 137/07, ss. 8-26.

Back to top